|  |  |  |
| --- | --- | --- |
|  | **MICHIGAN DEPARTMENT OF ENVIRONMENTAL QUALITY****AIR QUALITY DIVISION** |  |
| EFFECTIVE DATE: September 4, 2014REVISION DATE: June 16, 2016ISSUED TO**Grayling Generating Station Limited Partnership**State Registration Number (SRN): N2388LOCATED AT 4400 West Four Mile Road, Grayling, Crawford County, Michigan 49738 |
|  |

|  |
| --- |
| **RENEWABLE OPERATING PERMIT**Permit Number: MI-ROP-N2388-2014aExpiration Date: September 4, 2019Administratively Complete ROP Renewal Application Due Between March 4, 2018 and March 4, 2019This Renewable Operating Permit (ROP) is issued in accordance with and subject to Section 5506(3) of Part 55, Air Pollution Control, of the Natural Resources and Environmental Protection Act, 1994 PA 451, as amended (Act 451). Pursuant to Michigan Air Pollution Control Rule 210(1), this ROP constitutes the permittee’s authority to operate the stationary source identified above in accordance with the general conditions, special conditions and attachments contained herein. Operation of the stationary source and all emission units listed in the permit are subject to all applicable future or amended rules and regulations pursuant to Act 451 and the federal Clean Air Act. |

|  |
| --- |
| **SOURCE-WIDE PERMIT TO INSTALL**Permit Number: MI-PTI-N2388-2014aThis Permit to Install (PTI) is issued in accordance with and subject to Section 5505(5) of Act 451. Pursuant to Michigan Air Pollution Control Rule 214a, the terms and conditions herein, identified by the underlying applicable requirement citation of Rule 201(1)(a), constitute a federally enforceable PTI. The PTl terms and conditions do not expire and remain in effect unless the criteria of Rule 201(6) are met. Operation of all emission units identified in the PTI is subject to all applicable future or amended rules and regulations pursuant to Act 451 and the federal Clean Air Act. |

Michigan Department of Environmental Quality

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Janis Ransom, Cadillac District Supervisor

**TABLE OF CONTENTS**

[AUTHORITY AND ENFORCEABILITY 3](#_Toc453742359)

[A. GENERAL CONDITIONS 4](#_Toc453742360)

[Permit Enforceability 4](#_Toc453742361)

[General Provisions 4](#_Toc453742362)

[Equipment & Design 5](#_Toc453742363)

[Emission Limits 5](#_Toc453742364)

[Testing/Sampling 5](#_Toc453742365)

[Monitoring/Recordkeeping 6](#_Toc453742366)

[Certification & Reporting 6](#_Toc453742367)

[Permit Shield 7](#_Toc453742368)

[Revisions 8](#_Toc453742369)

[Reopenings 8](#_Toc453742370)

[Renewals 9](#_Toc453742371)

[Stratospheric Ozone Protection 9](#_Toc453742372)

[Risk Management Plan 9](#_Toc453742373)

[Emission Trading 9](#_Toc453742374)

[Permit To Install (PTI) 10](#_Toc453742375)

[B. SOURCE-WIDE CONDITIONS 11](#_Toc453742376)

[C. EMISSION UNIT CONDITIONS 14](#_Toc453742377)

[EMISSION UNIT SUMMARY TABLE 14](#_Toc453742378)

[EUBOILER 16](#_Toc453742379)

[EUEMERGENERATOR 24](#_Toc453742380)

[D. FLEXIBLE GROUP CONDITIONS 26](#_Toc453742381)

[FLEXIBLE GROUP SUMMARY TABLE 26](#_Toc453742382)

[FGMATHLHDLG 27](#_Toc453742383)

[FGCIRICEMACT 29](#_Toc453742384)

[E. NON-APPLICABLE REQUIREMENTS 33](#_Toc453742385)

[APPENDICES 34](#_Toc453742386)

[Appendix 1: Abbreviations and Acronyms 34](#_Toc453742387)

[Appendix 2. Schedule of Compliance 35](#_Toc453742388)

[Appendix 3. Monitoring Requirements 35](#_Toc453742389)

[Appendix 4. Recordkeeping 35](#_Toc453742390)

[Appendix 5. Testing Procedures 35](#_Toc453742391)

[Appendix 6. Permits to Install 35](#_Toc453742392)

[Appendix 7. Emission Calculations 36](#_Toc453742393)

[Appendix 8. Reporting 36](#_Toc453742394)

[Appendix 9. Transport Rule (TR) Trading Program Title V Requirements 37](#_Toc453742395)

# AUTHORITY AND ENFORCEABILITY

For the purpose of this permit, the **permittee** is defined as any person who owns or operates an emission unit at a stationary source for which this permit has been issued. The **department** is defined in Rule 104(d) as the Director of the Michigan Department of Environmental Quality (MDEQ) or his or her designee.

The permittee shall comply with all specific details in the permit terms and conditions and the cited underlying applicable requirements. All terms and conditions in this ROP are both federally enforceable and state enforceable unless otherwise footnoted. Certain terms and conditions are applicable to most stationary sources for which an ROP has been issued. These general conditions are included in Part A of this ROP. Other terms and conditions may apply to a specific emission unit, several emission units which are represented as a flexible group, or the entire stationary source which is represented as a source-wide group. Special conditions are identified in Parts B, C, D and/or the appendices.

In accordance with Rule 213(2)(a), all underlying applicable requirements will be identified for each ROP term or condition. All terms and conditions that are included in a PTI are streamlined or subsumed, or is state only enforceable will be noted as such.

In accordance with Section 5507 of Act 451, the permittee has included in the ROP application a compliance certification, a schedule of compliance, and a compliance plan. For applicable requirements with which the source is in compliance, the source will continue to comply with these requirements. For applicable requirements with which the source is not in compliance, the source will comply with the detailed schedule of compliance requirements that are incorporated as an appendix in this ROP. Furthermore, for any applicable requirements effective after the date of issuance of this ROP, the stationary source will meet the requirements on a timely basis, unless the underlying applicable requirement requires a more detailed schedule of compliance.

Issuance of this permit does not obviate the necessity of obtaining such permits or approvals from other units of government as required by law.

# A. GENERAL CONDITIONS

## Permit Enforceability

* All conditions in this permit are both federally enforceable and state enforceable unless otherwise noted. **(R 336.1213(5))**
* Those conditions that are hereby incorporated in a state-only enforceable Source-Wide PTI pursuant to Rule 201(2)(d) are designated by footnote one. **(R 336.1213(5)(a), R 336.1214a(5))**
* Those conditions that are hereby incorporated in a federally enforceable Source-Wide PTI pursuant to Rule 201(2)(c) are designated by footnote two. **(R 336.1213(5)(b), R 336.1214a(3))**

## General Provisions

1. The permittee shall comply with all conditions of this ROP. Any ROP noncompliance constitutes a violation of Act 451, and is grounds for enforcement action, for ROP revocation or revision, or for denial of the renewal of the ROP. All terms and conditions of this ROP that are designated as federally enforceable are enforceable by the Administrator of the United States Environmental Protection Agency (USEPA) and by citizens under the provisions of the federal Clean Air Act (CAA). Any terms and conditions based on applicable requirements which are designated as “state-only” are not enforceable by the USEPA or citizens pursuant to the CAA. **(R 336.1213(1)(a))**
2. It shall not be a defense for the permittee in an enforcement action that it would have been necessary to halt or reduce the permitted activity in order to maintain compliance with the conditions of this ROP. **(R 336.1213(1)(b))**
3. This ROP may be modified, revised, or revoked for cause. The filing of a request by the permittee for a permit modification, revision, or termination, or a notification of planned changes or anticipated noncompliance does not stay any ROP term or condition. This does not supersede or affect the ability of the permittee to make changes, at the permittee’s own risk, pursuant to Rule 215 and Rule 216. **(R 336.1213(1)(c))**
4. The permittee shall allow the department, or an authorized representative of the department, upon presentation of credentials and other documents as may be required by law and upon stating the authority for and purpose of the investigation, to perform any of the following activities **(R 336.1213(1)(d))**:
	1. Enter, at reasonable times, a stationary source or other premises where emissions-related activity is conducted or where records must be kept under the conditions of the ROP.
	2. Have access to and copy, at reasonable times, any records that must be kept under the conditions of the ROP.
	3. Inspect, at reasonable times, any of the following:
		1. Any stationary source.
		2. Any emission unit.
		3. Any equipment, including monitoring and air pollution control equipment.
		4. Any work practices or operations regulated or required under the ROP.
	4. As authorized by Section 5526 of Act 451, sample or monitor at reasonable times substances or parameters for the purpose of assuring compliance with the ROP or applicable requirements.
5. The permittee shall furnish to the department, within a reasonable time, any information the department may request, in writing, to determine whether cause exists for modifying, revising, or revoking the ROP or to determine compliance with this ROP. Upon request, the permittee shall also furnish to the department copies of any records that are required to be kept as a term or condition of this ROP. For information which is claimed by the permittee to be confidential, consistent with the requirements of the 1976 PA 442, MCL §15.231 et seq., and known as the Freedom of Information Act, the person may also be required to furnish the records directly to the USEPA together with a claim of confidentiality. **(R 336.1213(1)(e))**
6. A challenge by any person, the Administrator of the USEPA, or the department to a particular condition or a part of this ROP shall not set aside, delay, stay, or in any way affect the applicability or enforceability of any other condition or part of this ROP. **(R 336.1213(1)(f))**
7. The permittee shall pay fees consistent with the fee schedule and requirements pursuant to Section 5522 of Act 451. **(R 336.1213(1)(g))**
8. This ROP does not convey any property rights or any exclusive privilege. **(R 336.1213(1)(h))**

## Equipment & Design

1. Any collected air contaminants shall be removed as necessary to maintain the equipment at the required operating efficiency. The collection and disposal of air contaminants shall be performed in a manner so as to minimize the introduction of contaminants to the outer air. Transport of collected air contaminants in Priority I and II areas requires the use of material handling methods specified in Rule 370(2). **(R 336.1370)**
2. Any air cleaning device shall be installed, maintained, and operated in a satisfactory manner and in accordance with the Michigan Air Pollution Control rules and existing law. **(R 336.1910)**

## Emission Limits

1. Unless otherwise specified in this ROP, the permittee shall comply with Rule 301, which states, in part, “Except as provided in subrules 2, 3, and 4 of this rule, a person shall not cause or permit to be discharged into the outer air from a process or process equipment a visible emission of a density greater than the most stringent of the following: **(R 336.1301(1))**
	1. A 6-minute average of 20 percent opacity, except for one 6-minute average per hour of not more than 27 percent opacity.
	2. A limit specified by an applicable federal new source performance standard.

The grading of visible emissions shall be determined in accordance with Rule 303.

1. The permittee shall not cause or permit the emission of an air contaminant or water vapor in quantities that cause, alone or in reaction with other air contaminants, either of the following:
	1. Injurious effects to human health or safety, animal life, plant life of significant economic value, or property.1 **(R 336.1901(a))**
	2. Unreasonable interference with the comfortable enjoyment of life and property.1**(R 336.1901(b))**

## Testing/Sampling

1. The department may require the owner or operator of any source of an air contaminant to conduct acceptable performance tests, at the owner’s or operator’s expense, in accordance with Rule 1001 and Rule 1003, under any of the conditions listed in Rule 1001(1). **(R 336.2001)**
2. Any required performance testing shall be conducted in accordance with Rule 1001(2), Rule 1001(3) and Rule 1003. **(R 336.2001(2), R 336.2001(3), R 336.2003(1))**
3. Any required test results shall be submitted to the Air Quality Division (AQD) in the format prescribed by the applicable reference test method within 60 days following the last date of the test. **(R 336.2001(5))**

## Monitoring/Recordkeeping

1. Records of any periodic emission or parametric monitoring required in this ROP shall include the following information specified in Rule 213(3)(b)(i), where appropriate. **(R 336.1213(3)(b))**
	1. The date, location, time, and method of sampling or measurements.
	2. The dates the analyses of the samples were performed.
	3. The company or entity that performed the analyses of the samples.
	4. The analytical techniques or methods used.
	5. The results of the analyses.
	6. The related process operating conditions or parameters that existed at the time of sampling or measurement.
2. All required monitoring data, support information and all reports, including reports of all instances of deviation from permit requirements, shall be kept and furnished to the department upon request for a period of not less than 5 years from the date of the monitoring sample, measurement, report or application. Support information includes all calibration and maintenance records and all original strip-chart recordings, or other original data records, for continuous monitoring instrumentation and copies of all reports required by the ROP. **(R 336.1213(1)(e), R 336.1213(3)(b)(ii))**

## Certification & Reporting

1. Except for the alternate certification schedule provided in Rule 213(3)(c)(iii)(B), any document required to be submitted to the department as a term or condition of this ROP shall contain an original certification by a Responsible Official which states that, based on information and belief formed after reasonable inquiry, the statements and information in the document are true, accurate, and complete. **(R 336.1213(3)(c))**
2. A Responsible Official shall certify to the appropriate AQD District Office and to the USEPA that the stationary source is and has been in compliance with all terms and conditions contained in the ROP except for deviations that have been or are being reported to the appropriate AQD District Office pursuant to Rule 213(3)(c). This certification shall include all the information specified in Rule 213(4)(c)(i) through (v) and shall state that, based on information and belief formed after reasonable inquiry, the statements and information in the certification are true, accurate, and complete. The USEPA address is: USEPA, Air Compliance Data - Michigan, Air and Radiation Division, 77 West Jackson Boulevard, Chicago, Illinois 60604. **(R 336.1213(4)(c))**
3. The certification of compliance shall be submitted annually for the term of this ROP as detailed in the special conditions, or more frequently if specified in an applicable requirement or in this ROP. **(R 336.1213(4)(c))**
4. The permittee shall promptly report any deviations from ROP requirements and certify the reports. The prompt reporting of deviations from ROP requirements is defined in Rule 213(3)(c)(ii) as follows, unless otherwise described in this ROP. **(R 336.1213(3)(c))**
	1. For deviations that exceed the emissions allowed under the ROP, prompt reporting means reporting consistent with the requirements of Rule 912 as detailed in Condition 25. All reports submitted pursuant to this paragraph shall be promptly certified as specified in Rule 213(3)(c)(iii).
	2. For deviations which exceed the emissions allowed under the ROP and which are not reported pursuant to Rule 912 due to the duration of the deviation, prompt reporting means the reporting of all deviations in the semiannual reports required by Rule 213(3)(c)(i). The report shall describe reasons for each deviation and the actions taken to minimize or correct each deviation.
	3. For deviations that do not exceed the emissions allowed under the ROP, prompt reporting means the reporting of all deviations in the semiannual reports required by Rule 213(3)(c)(i). The report shall describe the reasons for each deviation and the actions taken to minimize or correct each deviation.
5. For reports required pursuant to Rule 213(3)(c)(ii), prompt certification of the reports is described in Rule 213(3)(c)(iii) as either of the following: **(R 336.1213(3)(c))**
	1. Submitting a certification by a Responsible Official with each report which states that, based on information and belief formed after reasonable inquiry, the statements and information in the report are true, accurate, and complete.
	2. Submitting, within 30 days following the end of a calendar month during which one or more prompt reports of deviations from the emissions allowed under the ROP were submitted to the department pursuant to Rule 213(3)(c)(ii), a certification by a Responsible Official which states that, “based on information and belief formed after reasonable inquiry, the statements and information contained in each of the reports submitted during the previous month were true, accurate, and complete”. The certification shall include a listing of the reports that are being certified. Any report submitted pursuant to Rule 213(3)(c)(ii) that will be certified on a monthly basis pursuant to this paragraph shall include a statement that certification of the report will be provided within 30 days following the end of the calendar month.
6. Semiannually for the term of the ROP as detailed in the special conditions, or more frequently if specified, the permittee shall submit certified reports of any required monitoring to the appropriate AQD District Office. All instances of deviations from ROP requirements during the reporting period shall be clearly identified in the reports. **(R 336.1213(3)(c)(i))**
7. On an annual basis, the permittee shall report the actual emissions, or the information necessary to determine the actual emissions, of each regulated air pollutant as defined in Rule 212(6) for each emission unit utilizing the emissions inventory forms provided by the department. **(R 336.1212(6))**
8. The permittee shall provide notice of an abnormal condition, start-up, shutdown, or malfunction that results in emissions of a hazardous or toxic air pollutant which continue for more than one hour in excess of any applicable standard or limitation, or emissions of any air contaminant continuing for more than two hours in excess of an applicable standard or limitation, as required in Rule 912, to the appropriate AQD District Office. The notice shall be provided not later than two business days after the start-up, shutdown, or discovery of the abnormal conditions or malfunction. Notice shall be by any reasonable means, including electronic, telephonic, or oral communication. Written reports, if required under Rule 912, must be submitted to the appropriate AQD District Supervisor within 10 days after the start-up or shutdown occurred, within 10 days after the abnormal conditions or malfunction has been corrected, or within 30 days of discovery of the abnormal conditions or malfunction, whichever is first. The written reports shall include all of the information required in Rule 912(5) and shall be certified by a Responsible Official in a manner consistent with the CAA. **(R 336.1912)**

## Permit Shield

1. Compliance with the conditions of the ROP shall be considered compliance with any applicable requirements as of the date of ROP issuance, if either of the following provisions is satisfied. **(R 336.1213(6)(a)(i), R 336.1213(6)(a)(ii))**
	1. The applicable requirements are included and are specifically identified in the ROP.
	2. The permit includes a determination or concise summary of the determination by the department that other specifically identified requirements are not applicable to the stationary source.

Any requirements identified in Part E of this ROP have been identified as non-applicable to this ROP and are included in the permit shield.

1. Nothing in this ROP shall alter or affect any of the following:
	1. The provisions of Section 303 of the CAA, emergency orders, including the authority of the USEPA under Section 303 of the CAA. **(R 336.1213(6)(b)(i))**
	2. The liability of the owner or operator of this source for any violation of applicable requirements prior to or at the time of this ROP issuance. **(R 336.1213(6)(b)(ii))**
	3. The applicable requirements of the acid rain program, consistent with Section 408(a) of the CAA. **(R 336.1213(6)(b)(iii))**
	4. The ability of the USEPA to obtain information from a source pursuant to Section 114 of the CAA. **(R 336.1213(6)(b)(iv))**
2. The permit shield shall not apply to provisions incorporated into this ROP through procedures for any of the following:
	1. Operational flexibility changes made pursuant to Rule 215. **(R 336.1215(5))**
	2. Administrative Amendments made pursuant to Rule 216(1)(a)(i)-(iv). **(R 336.1216(1)(b)(iii))**
	3. Administrative Amendments made pursuant to Rule 216(1)(a)(v) until the amendment has been approved by the department. **(R 336.1216(1)(c)(iii))**
	4. Minor Permit Modifications made pursuant to Rule 216(2). **(R 336.1216(2)(f))**
	5. State-Only Modifications made pursuant to Rule 216(4) until the changes have been approved by the department. **(R 336.1216(4)(e))**
3. Expiration of this ROP results in the loss of the permit shield. If a timely and administratively complete application for renewal is submitted not more than 18 months, but not less than 6 months, before the expiration date of the ROP, but the department fails to take final action before the end of the ROP term, the existing ROP does not expire until the renewal is issued or denied, and the permit shield shall extend beyond the original ROP term until the department takes final action. **(R 336.1217(1)(c), R 336.1217(1)(a))**

## Revisions

1. For changes to any process or process equipment covered by this ROP that do not require a revision of the ROP pursuant to Rule 216, the permittee must comply with Rule 215. **(R 336.1215, R 336.1216)**
2. A change in ownership or operational control of a stationary source covered by this ROP shall be made pursuant to Rule 216(1). **(R 336.1219(2))**
3. For revisions to this ROP, an administratively complete application shall be considered timely if it is received by the department in accordance with the time frames specified in Rule 216. **(R 336.1210(10))**
4. Pursuant to Rule 216(1)(b)(iii), Rule 216(2)(d) and Rule 216(4)(d), after a change has been made, and until the department takes final action, the permittee shall comply with both the applicable requirements governing the change and the ROP terms and conditions proposed in the application for the modification. During this time period, the permittee may choose to not comply with the existing ROP terms and conditions that the application seeks to change. However, if the permittee fails to comply with the ROP terms and conditions proposed in the application during this time period, the terms and conditions in the ROP are enforceable. **(R 336.1216(1)(c)(iii), R 336.1216(2)(d), R 336.1216(4)(d))**

## Reopenings

1. A ROP shall be reopened by the department prior to the expiration date and revised by the department under any of the following circumstances:
	1. If additional requirements become applicable to this stationary source with three or more years remaining in the term of the ROP, but not if the effective date of the new applicable requirement is later than the ROP expiration date. **(R 336.1217(2)(a)(i))**
	2. If additional requirements pursuant to Title IV of the CAA become applicable to this stationary source. **(R 336.1217(2)(a)(ii))**
	3. If the department determines that the ROP contains a material mistake, information required by any applicable requirement was omitted, or inaccurate statements were made in establishing emission limits or the terms or conditions of the ROP. **(R 336.1217(2)(a)(iii))**
	4. If the department determines that the ROP must be revised to ensure compliance with the applicable requirements. **(R 336.1217(2)(a)(iv))**

## Renewals

1. For renewal of this ROP, an administratively complete application shall be considered timely if it is received by the department not more than 18 months, but not less than 6 months, before the expiration date of the ROP. **(R 336.1210(8))**

## Stratospheric Ozone Protection

1. If the permittee is subject to Title 40 of the Code of Federal Regulations (CFR), Part 82 and services, maintains, or repairs appliances except for motor vehicle air conditioners (MVAC), or disposes of appliances containing refrigerant, including MVAC and small appliances, or if the permittee is a refrigerant reclaimer, appliance owner or a manufacturer of appliances or recycling and recovery equipment, the permittee shall comply with all applicable standards for recycling and emissions reduction pursuant to 40 CFR, Part 82, Subpart F.
2. If the permittee is subject to 40 CFR, Part 82, and performs a service on motor (fleet) vehicles when this service involves refrigerant in the MVAC, the permittee is subject to all the applicable requirements as specified in 40 CFR, Part 82, Subpart B, Servicing of Motor Vehicle Air Conditioners. The term “motor vehicle” as used in Subpart B does not include a vehicle in which final assembly of the vehicle has not been completed by the original equipment manufacturer. The term MVAC as used in Subpart B does not include the air-tight sealed refrigeration system used for refrigerated cargo or an air conditioning system on passenger buses using Hydrochlorofluorocarbon-22 refrigerant.

## Risk Management Plan

1. If subject to Section 112(r) of the CAA and 40 CFR, Part 68, the permittee shall register and submit to the USEPA the required data related to the risk management plan for reducing the probability of accidental releases of any regulated substances listed pursuant to Section 112(r)(3) of the CAA as amended in 40 CFR, Part 68.130. The list of substances, threshold quantities, and accident prevention regulations promulgated under 40 CFR, Part 68, do not limit in any way the general duty provisions under Section 112(r)(1).
2. If subject to Section 112(r) of the CAA and 40 CFR, Part 68, the permittee shall comply with the requirements of 40 CFR, Part 68, no later than the latest of the following dates as provided in 40 CFR, Part 68.10(a):
	1. June 21, 1999,
	2. Three years after the date on which a regulated substance is first listed under 40 CFR, Part 68.130, or
	3. The date on which a regulated substance is first present above a threshold quantity in a process.
3. If subject to Section 112(r) of the CAA and 40 CFR, Part 68, the permittee shall submit any additional relevant information requested by any regulatory agency necessary to ensure compliance with the requirements of 40 CFR, Part 68.
4. If subject to Section 112(r) of the CAA and 40 CFR, Part 68, the permittee shall annually certify compliance with all applicable requirements of Section 112(r) as detailed in Rule 213(4)(c)). **(40 CFR, Part 68)**

## Emission Trading

1. Emission averaging and emission reduction credit trading are allowed pursuant to any applicable interstate or regional emission trading program that has been approved by the Administrator of the USEPA as a part of Michigan’s State Implementation Plan. Such activities must comply with Rule 215 and Rule 216. **(R 336.1213(12))**

## Permit To Install (PTI)

1. The process or process equipment included in this permit shall not be reconstructed, relocated, or modified unless a PTI authorizing such action is issued by the department, except to the extent such action is exempt from the PTI requirements by any applicable rule. 2 **(R 336.1201(1))**
2. The department may, after notice and opportunity for a hearing, revoke PTI terms or conditions if evidence indicates the process or process equipment is not performing in accordance with the terms and conditions of the PTI or is violating the department’s rules or the CAA. 2 **(R 336.1201(8), Section 5510 of Act 451)**
3. The terms and conditions of a PTI shall apply to any person or legal entity that now or hereafter owns or operates the process or process equipment at the location authorized by the PTI. If a new owner or operator submits a written request to the department pursuant to Rule 219 and the department approves the request, this PTI will be amended to reflect the change of ownership or operational control. The request must include all of the information required by Subrules (1)(a), (b) and (c) of Rule 219. The written request shall be sent to the appropriate AQD District Supervisor, MDEQ. 2**(R 336.1219)**
4. If the installation, reconstruction, relocation, or modification of the equipment for which PTI terms and conditions have been approved has not commenced within 18 months of the original PTI issuance date, or has been interrupted for 18 months, the applicable terms and conditions from that PTI, as incorporated into the ROP, shall become void unless otherwise authorized by the department. Furthermore, the person to whom that PTI was issued, or the designated authorized agent, shall notify the department via the Supervisor, Permit Section, MDEQ, AQD, P. O. Box 30260, Lansing, Michigan 48909, if it is decided not to pursue the installation, reconstruction, relocation, or modification of the equipment allowed by the terms and conditions from that PTI. 2 **(R 336.1201(4))**

**Footnotes:**

1This condition is state-only enforceable and was established pursuant to Rule 201(1)(b).

2This condition is federally enforceable and was established pursuant to Rule 201(1)(a).

# B. SOURCE-WIDE CONDITIONS

Part B outlines the Source-Wide Terms and Conditions that apply to this stationary source. The permittee is subject to these special conditions for the stationary source in addition to the general conditions in Part A and any other terms and conditions contained in this ROP.

The permittee shall comply with all specific details in the special conditions and the underlying applicable requirements cited. If a specific condition type does not apply to this source, NA (not applicable) has been used in the table. If there are no Source-Wide Conditions, this section will be left blank.

**SOURCE-WIDE CONDITIONS**

**POLLUTION CONTROL EQUIPMENT**

NA

**I. EMISSION LIMIT(S)**

| **Pollutant** | **Limit** | **Time Period/ Operating Scenario** | **Equipment** | **Monitoring/****Testing Method** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- | --- | --- |
| NA | NA | NA | NA | NA | NA |

**II. MATERIAL LIMIT(S)**

| **Material** | **Limit** | **Time Period/ Operating Scenario** | **Equipment** | **Monitoring/****Testing Method** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- | --- | --- |
| NA | NA | NA | NA | NA | NA |

**III. PROCESS/OPERATIONAL RESTRICTION(S)**

1. The permittee shall maintain a program of fugitive dust control for all material storage piles, and all material handling equipment, all plant roadways, and the plant yard as approved by the District Supervisor. Changes to the program may be made upon approval by the AQD District Supervisor.2 **(R 336.1331(1)(c), R 336.1372)**
2. The permittee shall not operate EUBOILER unless a Malfunction Abatement Plan (MAP) is implemented and maintained. 2  **(R 336.1911)**

**IV. DESIGN/EQUIPMENT PARAMETER(S)**

NA

**V. TESTING/SAMPLING**

Records shall be maintained on file for a period of five years. **(R 336.1213(3)(b)(ii))**

NA

**VI. MONITORING/RECORDKEEPING**

Records shall be maintained on file for a period of five years. **(R 336.1213(3)(b)(ii))**

1. Records of street and parking lot washing/sweeping shall be kept and maintained on site and made available to the AQD staff upon request. **(R 336.1213(3))**

**VII. REPORTING**

1. Prompt reporting of deviations pursuant to General Conditions 21 and 22 of Part A. **(R 336.1213(3)(c)(ii))**

2. Semiannual reporting of monitoring and deviations pursuant to General Condition 23 of Part A. The report shall be postmarked or received by the appropriate AQD District Office by March 15 for reporting period July 1 to December 31 and September 15 for reporting period January 1 to June 30. **(R 336.1213(3)(c)(i))**

3. Annual certification of compliance pursuant to General Conditions 19 and 20 of Part A. The report shall be postmarked or received by the appropriate AQD District Office by March 15 for the previous calendar year. **(R 336.1213(4)(c))**

**See Appendix 8**

**VIII. STACK/VENT RESTRICTION(S)**

The exhaust gases from the stacks listed in the table below shall be discharged unobstructed vertically upwards to the ambient air unless otherwise noted:

| **Stack & Vent ID** | **Maximum Exhaust Dimensions****(inches)** | **Minimum Height Above Ground****(feet)** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- |
| NA | NA | NA | NA |

**IX. OTHER REQUIREMENT(S)**

1. The provisions and procedures of the program for continuous fugitive emissions shall be reviewed by the permittee on a yearly basis and the permittee shall submit any updates/changes to the AQD District Supervisor for approval. **(R 336.1213(3))**
2. The Preventative Maintenance/Malfunction Abatement Plan shall be reviewed and updated (if necessary) on a yearly basis. Changes to this plan may be made upon approval from the AQD District Supervisor.2 **(R 336.1911)**

**Footnotes:**

1This condition is state only enforceable and was established pursuant to Rule 201(1)(b).

2This condition is federally enforceable and was established pursuant to Rule 201(1)(a).

# C. EMISSION UNIT CONDITIONS

Part C outlines terms and conditions that are specific to individual emission units listed in the Emission Unit Summary Table. The permittee is subject to the special conditions for each emission unit in addition to the General Conditions in Part A and any other terms and conditions contained in this ROP.

The permittee shall comply with all specific details in the special conditions and the underlying applicable requirements cited. If a specific condition type does not apply, NA (not applicable) has been used in the table. If there are no conditions specific to individual emission units, this section will be left blank.

## EMISSION UNIT SUMMARY TABLE

The descriptions provided below are for informational purposes and do not constitute

enforceable conditions.

| **Emission Unit ID** | **Emission Unit Description****(Including Process Equipment & Control Device(s))** | **Installation****Date/****Modification Date** | **Flexible Group ID** |
| --- | --- | --- | --- |
| EUBOILER | This emission unit consists of one 523 MM Btu/hr. wood and tire-derived-fuel (TDF) fired boiler used to produce steam and equipped with natural gas auxiliary burners. The boiler is of a spreader-stroker design, and is equipped with a multi clone dust collector in order to capture and re-inject fly ash, an electrostatic precipitator (ESP) for the control of particulate matter, and a selective non-catalytic reduction (SNCR) system for the control of nitrogen oxides. The steam is used to produce approximately 36 megawatts of electricity at full capacity.  | 1/5/1992 | NA |
| EUEMERGENERATOR | This emission unit consists of one 6,188,000 Btu/hr. diesel-fired reciprocating internal combustion engine. The unit is standby diesel fired emergency generator used to provide electricity to the facility on an emergency basis.  | 1/5/1992 |  FGCIRICEMACT |
| EUFIREPUMP | This emission unit consists of one 1,040,000 Btu/hr. diesel-fired reciprocating internal combustion engine. The diesel fired engine is used to run a fire suppression system.  | 1/5/1992 | FGCIRICEMACT |
| EURAWMATL-HDLG | The raw material handling group includes the wood fuel pile, the wood conveyor, the TDF pile, and the TDF conveyor. Trucks supplying the wood to the facility unload at the wood fuel pile. Bulldozers transport the wood from the pile to the feed area of the wood conveyor. The TDF is taken from the pile and transferred to a TDF hopper by way of a front end loader. The TDF hopper feeds a conveyor that drops TDF onto the conveyor carrying wood to the boiler. The wood conveyor transfers the wood and TDF to the feed hopper of the boiler. | 1/5/1992 | FGMATHDLG |
| EUASH-HDLG | The ash material handling group includes the ash conveyors and the ash storage building. The fly ash removed from the boiler exhaust gases by the ESP is collected in a hopper under the ESP.  | 1/5/1992 | FGMATHDLG |

## EUBOILER

**EMISSION UNIT CONDITIONS**

**DESCRIPTION**

This emission unit consists of one 523 MM Btu/hr. wood and TDF fired boiler equipped with natural gas auxiliary burners. The boiler is of a spreader-stroker design. The steam is used to produce approximately 36 megawatts of electricity at full capacity.

**Flexible Group ID:** NA

**POLLUTION CONTROL EQUIPMENT**

The boiler is equipped with a multi clone dust collector in order to capture and re-inject fly ash, an ESP for the control of particulate matter, and a SNCR system for the control of nitrogen oxide.

**I. EMISSION LIMIT(S)**

| **Pollutant** | **Limit** | **Time Period/ Operating Scenario** | **Equipment** | **Monitoring/****Testing Method** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- | --- | --- |
| 1. Particulate
 | 0.03 pounds per million Btu (lb/MMBtu) heat input2a | Test Protocol\* | EUBOILER | SC V.1 | **40 CFR 52.21(c),(d),&(j), R 336.1331(1)(c)** |
| 1. Particulate
 | 12.0 pounds per hour2 | Test Protocol\* | EUBOILER | SC V.1 | **40 CFR 52.21(c),(d),&(j), R 336.1331(1)(c)** |
| 1. Particulate
 | 25.2 tons per year2 | 12-month rolling time period | EUBOILER | SC VI. 16 | **40 CFR 52.21(j), R 336.1331(1)(c)** |
| 1. Visible emissions
 | 10% opacity, except for one 6-minute average per hour of not more than 20% opacity.2b | 6-minute average | EUBOILER | SC VI. 7 | **40 CFR 52.21(c),(d),&(j), R 336.1301(1)(c)** |
| 1. Nitrogen Oxides
 | 0.15 lb/MMBtu heat input2c | 30-day rolling average | EUBOILER | SC VI. 1, SC VI. 15 | **40 CFR 52.21(j)** |
| 1. Nitrogen Oxides
 | 78.5 pounds per hour2 | 30-day rolling average | EUBOILER | SC VI. 1,SC VI. 15 | **40 CFR 52.21(j)** |
| 1. Nitrogen Oxides
 | 343.6 tons per year2 | 12-month rolling time period | EUBOILER | SC VI. 14 | **40 CFR 52.21 (c)(d)&(j)** |
| 1. Carbon Monoxide
 | 0.40 lb/MMBtu heat input2c | 24-hour rolling average | EUBOILER | SC VI. 2, SC VI. 15 | **40 CFR 52.21 (d)&(j)** |
| 1. Carbon Monoxide
 | 209.2 pounds per hour2 | 24-hour rolling average | EUBOILER | SC VI. 2, SC VI. 15 | **40 CFR 52.21 (d)&(j)** |
| 1. Carbon Monoxide
 | 916.3 tons per year2 | 12-month rolling time period | EUBOILER | SC VI. 14 | **40 CFR 52.21(j)** |
| 1. Volatile Organic Compounds
 | 0.017 lb/MMBtu heat input2 | Test Protocol\* | EUBOILER | SC V.1 | **40 CFR 52.21****(c),(d)&(j), R 336.1702(c)** |
| 1. Volatile Organic Compounds
 | 8.9 pounds per hour2 | Test Protocol\* | EUBOILER | SC V.1 | **40 CFR 52.21(j), R 336.1702(c)** |
| 1. Volatile Organic Compounds
 | 39.0 tons per year2 | 12-month rolling time period | EUBOILER | SC VI. 16 | **40 CFR 52.21(j),** **R 336.1702(c)** |
| 1. Sulfur Dioxide
 | 0.07 lb/MMBtu heat input2c | 24-hour rolling average | EUBOILER | SC VI. 3, SC VI. 4, SC VI. 15 | **40 CFR 52.21 (c)(d)&(j)** |
| 1. Sulfur Dioxide
 | 11.2 pounds per hour2 | 24-hour rolling average | EUBOILER | SC VI. 3, SC VI. 4, SC VI. 15 | **40 CFR 52.21 (c)(d)&(j)** |
| 1. Sulfur Dioxide
 | 39.0 tons per year2 | 12-month rolling time period | EUBOILER | SC VI. 14 | **40 CFR 52.21(j)** |
| 1. Lead
 | 0.02 pounds per hour2 | Test Protocol\* | EUBOILER | SC V.1 | **40 CFR 52.21(d),****R 336.1205** |
| 1. Lead
 | 0.10 tons per year2 | 12-month rolling time period | EUBOILER | SC VI. 16 | **40 CFR 52.21(d),** **R 336.1205** |
| 1. Sulfuric Acid Mist
 | 0.003 lb/MMBtu heat input2 | Test Protocol\* | EUBOILER | SC V.1 | **R 336.1225, R 336.1224, 40 CFR 52.21** |
| 1. Sulfuric Acid Mist
 | 1.5 pounds per hour2 | Test Protocol\* | EUBOILER | SC V.1 | **R 336.1225, R 336.1224, 40 CFR 52.21(c)(d)&(j)** |
| 1. Sulfuric Acid Mist
 | 6.6 tons per year2 | 12-month rolling time period | EUBOILER | SC VI. 16 | **R 336.1205, 40 CFR 52.21** |
| 1. Benzo(a)

pyrene | 0.005 pounds per hour1 | Test Protocol\* | EUBOILER | SC V.1 | **R 336.1225(1)** |
| 1. Arsenic
 | 0.02 pounds per hour1 | Test Protocol\* | EUBOILER | SC V.1 | **R 336.1225(1)** |
| 1. Cadmium
 | 0.012 pounds per hour1 | Test Protocol\* | EUBOILER | SC V.1 | **R 336.1225(1)** |
| 1. Chromium (total)
 | 0.012 pounds per hour1 | Test Protocol\* | EUBOILER | SC V.1 | **R 336.1225(1)** |
| 1. Manganese
 | 0.061 pounds per hour1 | Test Protocol\* | EUBOILER | SC V.1 | **R 336.1225(1)** |
| 1. Zinc Oxide, measured as Zinc
 | 9.5 pounds per hour1 | Test Protocol\* | EUBOILER | SC V.1 | **R 336.1225(1)** |

\* Test Protocol shall specify the averaging time period.

a In accordance with Rule 213(2) and Rule 213(6), compliance with this streamlined particulate limit shall be

considered compliance with the particulate limit established by **40 CFR 52.21(c),(d)&(j) and R 336.1331(1)(c);** and also compliance with the particulate limit in **40 CFR 60.43b(c)(1),** an additional applicable requirement that has been subsumed within this condition.

b In accordance with Rule 213(2) and Rule 213(6), compliance with this streamlined visible emissions limit shall be

considered compliance with the visible emissions limit established by **40 CFR 52.21(c),(d)&(j) and R 336.1301(1)(c);** and also compliance with the particulate limit in **40 CFR 60.43b(f),** an additional applicable requirement that has been subsumed within this condition.

c These emission rates do not include periods of startup or shutdown as defined in Condition III.3. and malfunction as defined in Rule 336.1113(a).

**II. MATERIAL LIMIT(S)**

| **Material** | **Limit** | **Time Period/ Operating Scenario** | **Equipment** | **Monitoring/****Testing Method** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- | --- | --- |
| 1. Natural Gas
 | 53,500 Standard cubic feet per hour2 | 24-hour daily average | EUBOILER | SC VI. 8 | **40 CFR 60.44b(d)** |
| 1. Tire Derived Fuel (TDF)
 | 3,750 pounds per hour1  | 24-hour daily average | EUBOILER | SC VI. 8 | **R 336.1225** |

**III. PROCESS/OPERATIONAL RESTRICTION(S)**

1. Except as allowed in the Preventative Maintenance/Malfunction Abatement Plan, the permittee shall not operate the EUBOILER unless the mechanical dust collectors, the electrostatic precipitator for removal of entrained particulates, and selective non-catalytic reduction system for NOx removal, are installed and operating properly.2 **(R 336.1910, R 336.1911)**
2. The permittee shall begin firing the EUBOILER from a cold start on natural gas only.2 **(R 336.1912)**
3. Startup is defined as the period of time from initiation of combustion firing until EUBOILER reaches steady state operation as measured by achieving three consecutive one hour averages of at least 25 percent of the design fuel flow rate for solid fuel. Shutdown is defined as that period of time from the initial lowering of the EUBOILER output with the intention of shutting down until the point at which the combustion process has stopped.2 **(R 336.1201)**
4. The permittee shall conduct a biennial tune-up of EUBOILER no more than 25 months after the previous tune-up. The tune-up shall consist of the following major elements: 1) Optimize total emissions of carbon monoxide (CO), consistent with any nitrogen oxide requirement to which the unit is subject, 2) Measure the concentrations of CO (ppmv) and oxygen (O2) (Vol-%) before and after the adjustments are made, ensuring that a consistent moisture basis is used for the measurements before and after the adjustments, 3) Maintain on-site and submit, if requested, a report listing the CO and O2 concentration measurements before and after the tune-up, a description of corrective actions taken as part of the tune-up and the type and amount of fuel used over the 12-months prior to the tune-up. If the EUBOILER is not operating on the required date for a tune-up, the tune-up must be conducted within 30 days of startup. **(40 CFR 63.11223(b))**

**IV. DESIGN/EQUIPMENT PARAMETER(S)**

1. The span value of all CEMS and COMS shall be 2.0 times the lowest emission standard or as specified in the federal regulations.2 **(40 CFR 60.13, 40 CFR, Part 75)**
2. The CEMS shall be installed, calibrated, maintained, and operated in accordance with the procedures set forth in 40 CFR 60.13 and Appendix B, 40 CFR, Part 60, or 40 CFR, Part 75, as appropriate.2 **(40 CFR 60.13, 40 CFR Part 75, R 336.1213(3))**
3. The permittee shall monitor and record the visible emissions from the EUBOILER on a continuous basis in a manner and with instrumentation acceptable to the AQD.2 **(40 CFR 60.13, 40 CFR 60.48b(a), 40 CFR 64.6(c)(1)(iii), 40 CFR 60.49(f))**
4. The COMS shall be calibrated, maintained, and operated in accordance with the procedures set forth in 40 CFR 60.13 and applicable Performance Specifications located in Appendix B, 40 CFR, Part 60.2 **(40 CFR 60.13, 40 CFR 48b(a))**

**V. TESTING/SAMPLING**

Records shall be maintained on file for a period of five years. **(R 336.1213(3)(b)(ii))**

1. Every five years, the permittee shall conduct verification of the following air contaminant emission rates from EUBOILER when firing wood, and a mixture of wood with TDF, by testing at owner’s expense.2
**(R 336.1213(3), R 336.2001, R 336.1225, 40 CFR 60.43b, 40 CFR 60.46b)**
	1. Particulate Matter (PM)
	2. Volatile Organic Compounds (VOC)
	3. Lead
	4. Sulfuric acid mist
	5. Arsenic
	6. Cadmium
	7. Chromium (total)
	8. Manganese
	9. Zinc Oxide, measured as zinc
	10. Benzo(a)pyrene
2. Stack testing procedures and the location of stack testing ports shall be in accordance with the applicable federal Reference Methods, 40 CFR, Part 60, Appendix A or other AQD approved methodology.2

**(40 CFR, Part 60, Appendix A, 40 CFR 60.43b, R 336.2003, R 336.2004)**

1. The permittee shall perform an annual audit of the COMS using the procedures set forth in USEPA Publication 450/4-92-010, “Performance Audits Procedures for Opacity Monitors”, or a procedure acceptable to the AQD.2 **(40 CFR 64.3(b)(3), R 336.1213(3))**
2. The permittee shall perform the quality assurance procedures of the CEMS as set forth in Appendix F of 40 CFR, Part 60 or 40 CFR, Part 75, as appropriate.2 **(40 CFR 60.13(a) 40 CFR, Part 75, R 336.1213(3))**

**VI. MONITORING/RECORDKEEPING**

Records shall be maintained on file for a period of five years. **(R 336.1213(3)(b)(ii))**

1. The permittee shall monitor and record the nitrogen oxides emissions, sulfur dioxide emissions, carbon dioxide concentration and exhaust flow rate of EUBOILER on a continuous basis in accordance with 40 CFR, Part 752. **(40 CFR, Part 75, 40 CFR 60.13, R 336.1213(3))**
2. The permittee shall monitor and record the carbon monoxide emission rate of the exhaust gases from EUBOILER on a continuous basis in a manner and with instrumentation acceptable to the AQD. **(R 336.1213(3), 40 CFR Part 60, Appendix B and Appendix F)**
3. The permittee shall monitor and record the amounts of TDF, wood, and natural gas fired in EUBOILER based upon a 24-hour daily average in a manner acceptable to the AQD.2 **(R 336.1213(3)(b)(ii), 40 CFR 60.49b(d), R 336.1225)**
4. The permittee shall calculate the annual capacity factor individually for natural gas and wood. The annual capacity factor is determined on a 12-month rolling average basis with a new annual capacity factor calculated at the end of each calendar month.2  **(40 CFR 60.49b(d), R 336.1213(3))**
5. The permittee shall calculate the annual capacity factor for tire derived fuel. The annual capacity factor is determined on a 12-month rolling average basis with a new annual capacity factor calculated at the end of each calendar month.2 **(R 336.1213(3))**
6. The permittee shall calculate the tons of sulfur dioxide, nitrogen oxides, and carbon monoxide emissions within 7 days after the end of each calendar month for the 12-month time period ending with that calendar month using data collected with the continuous emission monitors, and in a manner acceptable to the AQD.2 **(R 336.1213(3), R 336.1205(1)(a), 40 CFR 52.21)**
7. The permittee shall calculate the emissions of sulfur dioxide (24-hour rolling average), nitrogen oxides (30-day rolling average), and carbon monoxide (24-hour rolling average) on the basis indicated for each pollutant in a manner acceptable to the AQD.2 **(R 336.1213(3))**
8. For particulate matter, benzo-a-pyrene, Lead, Sulfuric acid mist, Arsenic, Cadmium, Chromium (total), Manganese, VOCs, and Zinc Oxide, measured as zinc, the permittee shall use emission factors from the most recent stack testing and the formula in Appendix 7 to calculate monthly emissions. The permittee shall calculate the tons of emissions within 7 days after the end of each calendar month for the 12-month time period ending with that calendar month using the monthly calculation from Appendix 7 and in a manner acceptable to the AQD.2 **(R 336.1213(3)(a)(ii))**
9. The permittee shall utilize COMS-recorded opacity as an indicator of the proper functioning of the ESP. The appropriate range of opacity defining proper function of the electrostatic precipitator is 0-5 percent opacity.

**(40 CFR 64.6(c)(1)(i and ii))**

1. The permittee shall use the COMS to assure compliance with the PM limit. An excursion for PM shall be two consecutive 1-hour block average opacity values greater than 5 percent. This condition does not affect compliance with R 336.1301. **(40 CFR 64.6(c)(2))**
2. The permittee shall operate the COMS during all required periods when EUBOILER is operating. Data recorded during monitoring malfunctions, repair activities and QA/QC operations shall not be used for 40 CFR, Part 64 compliance. **(40 CFR 64.6(c)(3), 40 CFR 64.7(c))**
3. In response to an excursion of more than 5 percent opacity based on 2 or more consecutive 1-hour block averages, the permittee shall restore operation of EUBOILER (including the ESP and associated capture system) to its normal or usual manner of operation as expeditiously as practicable in accordance with good air pollution control practices for minimizing emissions. The response shall include minimizing the period of any startup, shutdown or malfunction and taking any necessary corrective actions to restore normal operation and prevent the likely recurrence of the cause of an excursion or exceedance (other than those caused by excused startup or shutdown conditions). Such actions may include initial inspection and evaluation, recording that operations returned to normal without operator action (such as through response by a computerized distribution control system), or any necessary follow-up actions to return operation to within the indicator range, designated condition, or below the applicable emission limitation or standard, as applicable. The permittee shall keep records of these actions. **(40 CFR 64.7(d))**
4. The permittee shall properly maintain the COMS including keeping necessary parts for routine repair of the monitoring equipment. **(40 CFR 64.7(b))**
5. Except for, as applicable, monitoring malfunctions, associated repairs, and required quality assurance or control activities (including, as applicable, calibration checks and required zero and span adjustments), the owner or operator shall conduct all monitoring in continuous operation (or shall collect data at all required intervals) at all times that EUBOILER is operating. Data recorded during monitoring malfunctions, associated repairs, and required quality assurance or control activities shall not be used for the purposes of this part, including data averages and calculations or fulfilling a minimum data availability requirement, if applicable. The owner or operator shall use all the data collected during all other periods in assessing the operating of the ESP and associated control system. A monitoring malfunction is any sudden, in frequent, not reasonably preventable failure of the monitoring to provide valid data.Monitoring failures that are caused in part by poor maintenance or careless operation are not malfunctions.” The permittee shall operate the COMS during all required periods when EUBOILER is operating. Data recorded during monitoring malfunctions, repair activities and QA/QC operations shall not be used for 40 CFR, Part 64 compliance. **(40 CFR 64.6(c)(3), 64.7(c))**
6. The permittee shall maintain the following records: 1) A copy of each notification and report submitted to comply with 40 CFR Part 63, Subpart JJJJJJ and all documentation supporting any Initial Notification or Notification of Compliance Status, 2) Records of the date of each boiler tune-up and the procedures followed for the tune-up (including the manufacturer’s specifications to which the boiler was tuned, if applicable), 3) Records documenting that the Tire Derived Fuel fired in EUBOILER is a listed non-waste under §241.4(a), and 4) A copy of the energy assessment report. **(40 CFR 63.11225(c))**

**See Appendix 7**

**VII. REPORTING**

1. Prompt reporting of deviations pursuant to General Conditions 21 and 22 of Part A. **(R 336.1213(3)(c)(ii))**
2. Semiannual reporting of monitoring and deviations pursuant to General Condition 23 of Part A. The report shall be postmarked or received by the appropriate AQD District Office by March 15 for reporting period July 1 to December 31 and September 15 for reporting period January 1 to June 30. **(R 336.1213(3)(c)(i))**
3. Annual certification of compliance pursuant to General Conditions 19 and 20 of Part A. The report shall be postmarked or received by the appropriate AQD District Office by March 15 for the previous calendar year. **(R 336.1213(4)(c))**
4. In accordance with 40 CFR, Parts 60.7(c) and (d) an excess emissions report (EER) and summary report shall be submitted in the format of Figure 1 in 40 CFR 60.7(d) within 30 days following the end of each calendar quarter for all CEMS and COMS. The EER shall include the following information:2 **(40 CFR 60.7, 40 CFR 75.65, 40 CFR 60.49b(h), R336.1213(3))**
5. A report of each exceedance of the opacity limit, and/or exceedance of an emission limit. This includes the date, time, magnitude, cause and corrective actions of all exceedances during the reporting period.
6. A report of all periods of COMS and/or CEMS downtime and corrective action.
7. A report of the total operating time of EUBOILER during the reporting period.
8. If no exceedances or COMS and/or CEMS downtime occurred during the reporting period, the permittee shall report that fact.
9. A report of any periods that the CEMS exceed the instrument range.
10. The permittee shall submit a complete test protocol to the AQD for approval at least 30 days prior to the anticipated test date.2 **(40 CFR 60.7, R336.1213(3))**
11. The permittee shall notify the AQD no less than 7 days prior to the anticipated test date. **(R 336.2001(3))**
12. Following verification of emissions rates for the air contaminants listed in Condition V.1, the permittee shall submit two complete test reports of the test results to the AQD, one to the Technical Programs Unit and one to the district office, within 60 days following the last date of the test. 2 **(40 CFR 60.8, R 336.1213(3))**
13. The permittee shall submit a summary of compliance with the monthly sulfur dioxide, nitrogen oxides, and carbon monoxide emission calculations for the previous 12-month rolling time period to the District Supervisor in an acceptable format within 30 days following the end of each quarter in which the data was collected.2
**(40 CFR 52.21, R 336.1213(3))**
14. The results of the annual audit of the COMS shall be submitted to the AQD District Supervisor within 60 days of completion.2 **(R 336.1213(3))**
15. Each calendar quarter, for the COMS and CEMS, the permittee shall report the results of the applicable Quality Assurance Procedures as set forth in Appendix F of 40 CFR, Part 60, or 40 CFR, Part 75 Appendix B, as appropriate. Within 30 days following the end of each quarter, the permittee shall submit the results to the AQD in the format of the data assessment report (Figure 1, Appendix F).2 **(40 CFR 60.13, 40 CFR, Part 60, Appendix F, 40 CFR 75, R 336.1213(3))**
16. Each semiannual report of monitoring and deviations shall include summary information on the number, duration and cause of excursions and/or exceedances and the corrective actions taken. If there were no excursions and/or exceedances in the reporting period, then this report shall include a statement that there were no excursions and/or exceedances. **(40 CFR 64.9(a)(2)(i))**
17. Each semiannual report of monitoring and deviations shall include summary information on COM downtime. If there were no periods of COM downtime in the reporting period, then this report shall include a statement that there were no periods of COM downtime. **(40 CFR 64.9(a)(2)(ii))**
18. By March 1 of each year, the permittee shall prepare, and submit upon request, an annual compliance certification report for the previous calendar year containing the following information: 1) Company name and address, 2) Statement by a responsible official (with the official’s name, title, phone number, email address and signature) certifying the truth, accuracy and completeness of the notification and a statement of whether the source has complied with all of the relevant standards and other requirements of 40 CFR Part 63, Subpart JJJJJJ. The notification must include the following certification statements: a) “This facility complies with the requirements of §63.11223 to conduct a biennial or 5-year tune-up, as applicable, of each boiler.” b) “”No secondary materials that are solid waste were combusted in any affected unit.” This report must be submitted by March 15 if there were any deviations from the applicable requirements during the reporting period, and the report must also include a description of the deviations, the time periods during which the deviations occurred, and the corrective actions which were taken. As an alternative, this report may be prepared on a biennial basis as opposed to annual basis. **(40 CFR 63.11225(b))**

**See Appendix 8**

**VIII. STACK/VENT RESTRICTION(S)**

The exhaust gases from the stacks listed in the table below shall be discharged unobstructed vertically upwards to the ambient air unless otherwise noted:

| **Stack & Vent ID** | **Maximum Exhaust Dimensions****(inches)** | **Minimum Height Above Ground****(feet)** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- |
| 1. SV89C36
 | 942 | 2202 | **40 CFR 52.21(c)&(d)** |

**IX. OTHER REQUIREMENT(S)**

1. The permittee shall not use wood or wood waste containing creosote, pentachlorophenol, or copper chromium arsenate as fuel.1 **(R 336.1225)**
2. The permittee shall promptly notify AQD for the need to modify the Compliance Assurance Monitoring Plan if the existing plan is found to be inadequate and shall submit a proposed modification to the ROP. **(40 CFR 64.7(e))**
3. The permittee shall comply with all applicable requirements of 40 CFR, Part 64. **(40 CFR, Part 64)**
4. The permittee shall comply with the provisions of the Transport Rule NOX Annual Trading Program, as specified in 40 CFR, Part 97 Subpart AAAAA, and identified in Appendix 9. **(40 CFR Part 97 Subpart AAAAA)**
5. The permittee shall comply with the provisions of the Transport Rule NOX Ozone Trading Program, as specified in 40 CFR, Part 97 Subpart BBBBB, and identified in Appendix 9. **(40 CFR Part 97 Subpart BBBBB)**
6. The permittee shall comply with the provisions of the Transport Rule SO2 Group 1 Trading Program, as specified in 40 CFR, Part 97 Subpart CCCCC, and identified in Appendix 9. **(40 CFR Part 97 Subpart CCCCC)**
7. The permittee shall comply with all applicable provisions of the National Emissions Standards for Hazardous Air Pollutants, as specified in 40 CFR, Part 63, Subparts A and JJJJJJ, for Industrial, Commercial and Institutional Boilers located at Area Sources of HAP Emissions. **(40 CFR, Part 63, Subparts A and JJJJJJ)**
8. The permittee shall comply with all applicable provisions of the Standards of Performance for Industrial, Commercial and Institutional Boilers, as specified in 40 CFR, Part 60, Subparts A and Db.
**(40 CFR, Part 63, Subparts A and Db)**
9. The permittee shall comply with all applicable provisions of the National Emissions Standards for Hazardous Air Pollutants, as specified in 40 CFR Part 63, Subparts A and JJJJJJ, for Industrial, Commercial and Institutional Boilers located at Area Sources of HAP Emissions. **(40 CFR Part 63, Subparts A and JJJJJJ)**

**Footnotes:**

1This condition is state only enforceable and was established pursuant to Rule 201(1)(b).

2This condition is federally enforceable and was established pursuant to Rule 201(1)(a).

## EUEMERGENERATOR

**EMISSION UNIT CONDITIONS**

**DESCRIPTION**

The emission unit consists of one diesel-fired reciprocating internal combustion engine. The unit is standby diesel fired emergency generator used to provide electricity to the facility on an emergency basis.

**Flexible Group ID:** NA

**POLLUTION CONTROL EQUIPMENT**

NA

**I. EMISSION LIMIT(S)**

| **Pollutant** | **Limit** | **Time Period/ Operating Scenario** | **Equipment** | **Monitoring/****Testing Method** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- | --- | --- |
| NA | NA | NA | NA | NA | NA |

**II. MATERIAL LIMIT(S)**

| **Material** | **Limit** | **Time Period/ Operating Scenario** | **Equipment** | **Monitoring/****Testing Method** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- | --- | --- |
| 1. Distillate Oil (Diesel Fuel)
 | Only use No. 1 or No. 2 distillate oil in the diesel generator2 | NA | EUEMERGENERATOR | SC VI.1 | **R 336.1401, R 336.1301(1)** |

**III. PROCESS/OPERATIONAL RESTRICTION(S)**

NA

**IV. DESIGN/EQUIPMENT PARAMETER(S)**

NA

**V. TESTING/SAMPLING**

Records shall be maintained on file for a period of five years. **(R 336.1213(3)(b)(ii))**

NA

**VI. MONITORING/RECORDKEEPING**

Records shall be maintained on file for a period of five years. **(R 336.1213(3)(b)(ii))**

1. The permittee shall keep records on each shipment of diesel fuel as to which grade of diesel was received. **(R 336.1213(3))**

**VII. REPORTING**

1. Prompt reporting of deviations pursuant to General Conditions 21 and 22 of Part A. **(R 336.1213(3)(c)(ii))**

2. Semiannual reporting of monitoring and deviations pursuant to General Condition 23 of Part A. The report shall be postmarked orreceived by the appropriate AQD District Office by March 15 for reporting period July 1 to December 31 and September 15 for reporting period January 1 to June 30. **(R 336.1213(3)(c)(i))**

1. Annual certification of compliance pursuant to General Conditions 19 and 20 of Part A. The report shall be postmarked or received by the appropriate AQD District Office by March 15 for the previous calendar year. **(R 336.1213(4)(c))**

**See Appendix 8**

**VIII. STACK/VENT RESTRICTION(S)**

The exhaust gases from the stacks listed in the table below shall be discharged unobstructed vertically upwards to the ambient air unless otherwise noted:

| **Stack & Vent ID** | **Maximum Exhaust Dimensions****(inches)** | **Minimum Height Above Ground****(feet)** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- |
| NA | NA | NA | NA |

**IX. OTHER REQUIREMENT(S)**

NA

**Footnotes:**

1 This condition is state only enforceable and was established pursuant to Rule 201(1)(b).

2 This condition is federally enforceable and was established pursuant to Rule 201(1)(a).

# D. FLEXIBLE GROUP CONDITIONS

Part D outlines the terms and conditions that apply to more than one emission unit. The permittee is subject to the special conditions for each flexible group in addition to the General Conditions in Part A and any other terms and conditions contained in this ROP.

The permittee shall comply with all specific details in the special conditions and the underlying applicable requirements cited. If a specific condition type does not apply, NA (not applicable) has been used in the table. If there are no special conditions that apply to more than one emission unit, this section will be left blank.

## FLEXIBLE GROUP SUMMARY TABLE

The descriptions provided below are for informational purposes and do not constitute

enforceable conditions.

| **Flexible Group ID** | **Flexible Group Description** | **Associated****Emission Unit IDs** |
| --- | --- | --- |
| FGMATLHDLG | This flexible consists of ash and wood handling.  | EUASH-HDLG, EURAWMATL-HDLG |
| FGCIRICEMACT | This flexible group consists of existing emergency compression ignition engines which are subject to 40 CFR, Part 63, Subpart ZZZZ. | EUEMERGENERATOR, EUFIREPUMP |

## FGMATHLHDLG

**FLEXIBLE GROUP CONDITIONS**

**DESCRIPTION**

This flexible group consists of raw material fuel handling including the wood fuel pile and the wood conveying system, and the equipment responsible for getting the raw material fuel from the storage piles and into the boiler by use of conveyors. This flexible group also consists of ash handling equipment including the conveyors that are used in handling the ash coming from the boiler and the ash storage building.

**Emission Units:** EURAWMATL-HDLG, EUASH-HDLG

**POLLUTION CONTROL EQUIPMENT**

Ash Storage Building, Ash Wetting System.

**I. EMISSION LIMIT(S)**

| **Pollutant** | **Limit** | **Time Period/ Operating Scenario** | **Equipment** | **Monitoring/****Testing Method** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- | --- | --- |
| 1. Visible emissions
 | 5 percent opacity2 | 6-minute average | EURAWMATL-HDLG, EUASH-HDLG  | SC VI.1 | **R 336.1301(1)(c)** |

**II. MATERIAL LIMIT(S)**

| **Material** | **Limit** | **Time Period/ Operating Scenario** | **Equipment** | **Monitoring/****Testing Method** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- | --- | --- |
| NA | NA | NA | NA | NA | NA |

**III. PROCESS/OPERATIONAL RESTRICTION(S)**

1. The applicant shall not operate the ash handling system unless the wetting system is operating properly.2 **(R 336.1910)**

**IV. DESIGN/EQUIPMENT PARAMETER(S)**

NA

**V. TESTING/SAMPLING**

Records shall be maintained on file for a period of five years. **(R 336.1213(3)(b)(ii))**

NA

**VI. MONITORING/RECORDKEEPING**

Records shall be maintained on file for a period of five years. **(R 336.1213(3)(b)(ii))**

1. Personnel shall observe ash-handling equipment and wood handling equipment at least once daily. If there are any visible emissions coming from these equipment personnel shall document and notify supervision. Repairs or remedial action are to be initiated within 24 hours and completed as expeditiously as possible.

Records of visible emissions observations, repairs, and remedial actions shall be kept and made available to the AQD upon request. **(R 336.1213(3))**

1. The permittee shall keep records of weekly inspections of equipment for FGMATLHDLG. These records shall include the corrective measures taken, if any, on the inspected equipment. These records shall be kept and maintained on site and be made available to the AQD staff upon request. **(R 336.1213(3))**

**VII. REPORTING**

1. Prompt reporting of deviations pursuant to General Conditions 21 and 22 of Part A. **(R 336.1213(3)(c)(ii))**

2. Semiannual reporting of monitoring and deviations pursuant to General Condition 23 of Part A. The report shall be postmarked or received by the appropriate AQD District Office by March 15 for reporting period July 1 to December 31 and September 15 for reporting period January 1 to June 30. **(R 336.1213(3)(c)(i))**

3. Annual certification of compliance pursuant to General Conditions 19 and 20 of Part A. The report shall be postmarked or received by the appropriate AQD District Office by March 15 for the previous calendar year. **(R 336.1213(4)(c))**

**VIII. STACK/VENT RESTRICTION(S)**

The exhaust gases from the stacks listed in the table below shall be discharged unobstructed vertically upwards to the ambient air unless otherwise noted:

| **Stack & Vent ID** | **Maximum Exhaust Dimensions****(inches)** | **Minimum Height Above Ground****(feet)** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- |
| NA | NA | NA | NA |

**IX. OTHER REQUIREMENT(S)**

NA

**Footnotes:**

1This condition is state only enforceable and was established pursuant to Rule 201(1)(b).

2This condition is federally enforceable and was established pursuant to Rule 201(1)(a).

## FGCIRICEMACT

**FLEXIBLE GROUP CONDITIONS**

**DESCRIPTION**

This flexible group includes emergency stationary compression ignition (CI) reciprocating internal combustion engines (RICE) located at an area source of hazardous air pollutants (HAPs) which were installed or reconstructed before June 12, 2006 (i.e., existing CI RICE).

**Emission Units:** EUEMERGENERATOR, EUFIREPUMP

**POLLUTION CONTROL EQUIPMENT**

NA

**I. EMISSION LIMIT(S)**

NA

I**I. MATERIAL LIMIT(S)**:

NA

**III. PROCESS/OPERATIONAL RESTRICTION(S)**

1. The permittee shall limit operation of each stationary emergency RICE as follows:
	1. Emergency stationary RICE may be operated for the purposes of maintenance checks, readiness testing and emergency demand response for up to 100 hours per year. **(40 CFR 63.6640(f))**
	2. Emergency stationary RICE may be operated up to 50 hours per year in non-emergency situations, but those hours are to be counted towards the 100 hours per year for maintenance, testing and emergency demand response. These 50 hours per year for non-emergency situations cannot be used for peak-shaving or non-emergency demand response, or to generate income for a facility to supply power to an electric grid or otherwise supply power as part of a financial arrangement with another entity. Any use of the engines for purposes of emergency demand response are to be counted towards the 100 hours per year for maintenance, testing and emergency demand response and must comply with 63.6640(f)(2)(ii) and (iii). **(40 CFR 63.6640(f))**
2. The permittee shall operate and maintain existing emergency stationary RICE according to the manufacturer's emission-related operation and maintenance instructions or a plan developed by the facility that provides for the maintenance and operation of the engine in a manner consistent with good air pollution control practice for minimizing emissions. **(40 CFR 63.6625(e) and 40 CFR 63.6640(a) and Table 6(9)(a))**
3. The permittee shall operate and maintain engine manufacturer installed after treatment control device(s) on existing emergency stationary RICE according to the manufacturer's emission-related operation and maintenance instructions or a plan developed by the facility that provides for the maintenance and operation of the engine in a manner consistent with good air pollution control practice for minimizing emissions.

**(40 CFR 63.6625(e))**

4. For existing emergency CI RICE, the permittee shall change the oil and filter every 500 hours of operation or annually, whichever comes first. In lieu of changing the oil and filter, the permittee may implement an oil analysis program to have the oil analyzed as described in 40 CFR 63.6625(i). **(40 CFR 63.6602, 40 CFR 63.6603(a) and Table 2d(4)(a))**

1. For existing emergency CI RICE, the permittee shall inspect the air cleaner every 1000 hours of operation or annually, whichever comes first. **(40 CFR 63.6602, 40 CFR 63.6603(a) and Table 2d(4)(b))**

6. If the analytical results of the oil analysis program for emergency stationary CI engines indicate any of the following limits are exceeded, the permittee shall change the oil within 2 days of receiving the results of the analysis. If the engine is not in operation when the results of the analysis are received, the permittee shall change the oil within 2 days or before commencing operation, whichever is later. **(40 CFR 63.6625(i))**

1. Total Base Number is less than 30 percent of the Total Base Number of the oil when new.
2. Viscosity of the oil has changed by more than 20 percent from the viscosity of the oil when new.
3. Percent water content (by volume) is greater than 0.5.

7. For existing emergency CI RICE, the permittee shall inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. **(40 CFR 63.6602, 40 CFR 63.6603(a) and Table 2d(4)(c))**

8. The permittee shall minimize the engine's time spent at idle during startup and minimize the engine's startup time to a period needed for appropriate safe loading of the engine, not to exceed 30 minutes, after which time the non-startup emission standards apply. **(40 CFR 63.6625(h) & 40 CFR 63.6640(a))**

1. If an emergency engine is operating during an emergency and it is not possible to shut down the engine in order to perform the management practice requirements on the schedule required in Conditions III.4-7, or if performing the management practice on the required schedule would otherwise pose an unacceptable risk under Federal, State, or local law, the management practice can be delayed until the emergency is over or the unacceptable risk under Federal, State, or local law has abated. The management practice should be performed as soon as practicable after the emergency has ended or the unacceptable risk under Federal, State, or local law has abated. Sources must report any failure to perform the management practice on the schedule required and the Federal, State or local law under which the risk was deemed unacceptable.

**(40 CFR, Part 63, Subpart ZZZZ, Table 2d, Footnote 2)**

**IV. DESIGN/EQUIPMENT PARAMETER(S)**

1. For existing emergency RICE with a site rating of 500 brake HP or less, the permittee shall install a non-resettable hour meter by May 3, 2013. **(40 CFR 63.6600(a), 40 CFR 63.6625(f), 40 CFR 63.6640)**

**V. TESTING/SAMPLING**

1. For the optional oil analysis program for emergency stationary CI engines, the permittee shall at a minimum analyze the oil for the following three parameters: **(40 CFR 63.6625(i))**

a. Total Base Number

b. Viscosity

c. Percent water content.

**VI. MONITORING/RECORDKEEPING**

Records shall be maintained on file for a period of five years. **(R336.1213(3)(b)(ii))**

1. The permittee shall maintain a copy of each notification and report submitted, including supporting documentation. **(40 CFR 63.6655(a)(1))**

2. The permittee shall maintain a record of the occurrence and duration of each malfunction of operation (i.e., process equipment) or the air pollution control and monitoring equipment. **(40 CFR 63.6655(a)(2))**

3. The permittee shall maintain a record of actions taken during periods of malfunction to minimize emissions in accordance with §63.6605(b), including corrective actions to restore malfunctioning process and air pollution control and monitoring equipment to its normal or usual manner of operation. **(40 CFR 63.6655(a)(5))**

4. The permittee shall maintain a record of all required maintenance performed on the air pollution control and monitoring equipment. **(40 CFR 63.6655(a)(4))**

5 The permittee shall maintain records of the maintenance conducted on the stationary RICE in order to demonstrate that the stationary RICE and after-treatment control device (if any) was operated and maintained according to the facility maintenance plan. **(40 CFR 63.6655(e)(3))**

6. For existing emergency stationary RICE that do not meet the emission standards applicable to non-emergency stationary RICE, permittee shall maintain records of the hours of operation of the engine that is recorded through the non-resettable hour meter. The records must document how many hours are spent for emergency operation; including what classified the operation as emergency and how many hours are spent for non-emergency operation. If the engines are used for emergency demand response operation, the owner or operator must keep records of the notification of the emergency situation, and the date, start time and end time the engine was operated as part of emergency demand response. **(40 CFR 63.6655(f))**

7. For the oil analysis program, the permittee shall keep records of the parameters that are analyzed as part of the program, the results of the analysis, and the oil changes for the engine. The analysis program must be part of the maintenance plan for the engine. **(40 CFR 63.6625(i&j))**

**VII. REPORTING**

* + - 1. Prompt reporting of deviations pursuant to General Conditions 21 and 22 of Part A. **(R336.1213(3)(c)(ii))**
			2. Semiannual reporting of monitoring and deviations pursuant to General Condition 23 of Part A. The report shall be postmarked or received by the appropriate AQD District Office by March 15 for reporting period July 1 to December 31 and September 15 for reporting period January 1 to June 30. **(R336.1213(3)(c)(i))**
			3. Annual certification of compliance pursuant to General Conditions 19 and 20 of Part A. The report shall be postmarked or received by the appropriate AQD District Office by March 15 for the previous calendar year. **(R336.1213(4)(c))**
1. Sources must report any failure to perform the management practice (i.e., oil and filter changes, air filter inspections, hoses and belt inspections) on the schedule required and the Federal, State or local law under which the risk was deemed unacceptable.  **(40 CFR, Part 63, Subpart ZZZZ, Table 2d, Footnote 2)**

**VIII. STACK/VENT RESTRICTION(S)**

The exhaust gases from the stacks listed in the table below shall be discharged unobstructed vertically upwards to the ambient air unless otherwise noted:

| **Stack & Vent ID** | **Maximum Exhaust Dimensions****(inches)** | **Minimum Height Above Ground****(feet)** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- |
| NA | NA | NA | NA |

**IX. OTHER REQUIREMENT(S)**

1. The permittee shall comply with all applicable provisions of the National Emissions Standards for Hazardous Air Pollutants, as specified in 40 CFR, Part 63, Subparts A and ZZZZ, for Stationary Reciprocating Internal Combustion Engines. **(40 CFR 63.6595(a)(1), 40 CFR, Part 63, Subparts A and ZZZZ)**

**Footnotes:**

1This condition is state only enforceable and was established pursuant to Rule 201(1)(b).

2This condition is federally enforceable and was established pursuant to Rule 201(1)(a).

# E. NON-APPLICABLE REQUIREMENTS

At the time of the ROP issuance, the AQD has determined that the requirements identified in the table below are not applicable to the specified emission unit(s) and/or flexible group(s). This determination is incorporated into the permit shield provisions set forth in the General Conditions in Part A pursuant to Rule 213(6)(a)(ii). If the permittee makes a change that affects the basis of the non-applicability determination, the permit shield established as a result of that non-applicability decision is no longer valid for that emission unit or flexible group.

|  |
| --- |
| APPENDICES |

## Appendix 1: Abbreviations and Acronyms

The following is an alphabetical listing of abbreviations/acronyms that may be used in this permit.

|  |  |  |  |
| --- | --- | --- | --- |
| AQD | Air Quality Division | MM | Million |
| acfm | Actual cubic feet per minute | MSDS | Material Safety Data Sheet |
| BACT | Best Available Control Technology | MW | Megawatts |
| BTU | British Thermal Unit | NA | Not Applicable |
| °C | Degrees Celsius | NAAQS | National Ambient Air Quality Standards |
| CAA | Federal Clean Air Act | NESHAP | National Emission Standard for Hazardous Air Pollutants |
| CAM | Compliance Assurance Monitoring | NMOC | Non-methane Organic Compounds |
| CEM  | Continuous Emission Monitoring | NOx | Oxides of Nitrogen |
| CFR | Code of Federal Regulations | NSPS | New Source Performance Standards |
| CO | Carbon Monoxide | NSR | New Source Review |
| COM | Continuous Opacity Monitoring | PM | Particulate Matter  |
| department | Michigan Department of Environmental Quality  | PM-10 | Particulate Matter less than 10 microns in diameter |
| dscf | Dry standard cubic foot | pph | Pound per hour |
| dscm | Dry standard cubic meter | ppm | Parts per million |
| EPA | United States Environmental Protection Agency | ppmv | Parts per million by volume  |
| EU | Emission Unit | ppmw | Parts per million by weight  |
| °F | Degrees Fahrenheit | PS | Performance Specification |
| FG | Flexible Group | PSD | Prevention of Significant Deterioration |
| GACS | Gallon of Applied Coating Solids | psia | Pounds per square inch absolute |
| GC | General Condition | psig | Pounds per square inch gauge  |
| gr  | Grains | PeTE | Permanent Total Enclosure |
| HAP | Hazardous Air Pollutant | PTI | Permit to Install |
| Hg | Mercury  | RACT | Reasonable Available Control Technology |
| hr | Hour  | ROP | Renewable Operating Permit |
| HP | Horsepower  | SC | Special Condition |
| H2S | Hydrogen Sulfide | scf | Standard cubic feet |
| HVLP | High Volume Low Pressure \* | sec | Seconds  |
| ID  | Identification (Number) | SCR | Selective Catalytic Reduction |
| IRSL | Initial Risk Screening Level | SO2 | Sulfur Dioxide  |
| ITSL | Initial Threshold Screening Level | SRN | State Registration Number |
| LAER | Lowest Achievable Emission Rate  | TAC | Toxic Air Contaminant |
| lb | Pound | Temp | Temperature |
| m | Meter | THC | Total Hydrocarbons |
| MACT | Maximum Achievable Control Technology  | tpy | Tons per year |
| MAERS | Michigan Air Emissions Reporting System | µg  | Microgram  |
| MAP | Malfunction Abatement Plan | VE | Visible Emissions |
| MDEQ | Michigan Department of Environmental Quality | VOC | Volatile Organic Compounds  |
| mg | Milligram  | yr | Year  |
| mm | Millimeter |  |  |

\*For HVLP applicators, the pressure measured at the gun air cap shall not exceed 10 pounds per square inch gauge (psig).

## Appendix 2. Schedule of Compliance

The permittee certified in the ROP application that this stationary source is in compliance with all applicable requirements and the permittee shall continue to comply with all terms and conditions of this ROP. A Schedule of Compliance is not required. **(R 336.1213(4)(a), R 336.1119(a)(ii))**

## Appendix 3. Monitoring Requirements

Specific monitoring requirement procedures, methods or specifications are detailed in Part A or the appropriate Source-Wide, Emission Unit and/or Flexible Group Special Conditions. Therefore, this appendix is not applicable.

## Appendix 4. Recordkeeping

Specific recordkeeping requirement formats and procedures are detailed in Part A or the appropriate source-wide, emission unit and/or flexible group special conditions. Therefore, this appendix is not applicable.

## Appendix 5. Testing Procedures

Specific testing requirement plans, procedures, and averaging times are detailed in the appropriate Source-Wide, Emission Unit and/or Flexible Group Special Conditions. Therefore, this appendix is not applicable.

## Appendix 6. Permits to Install

The following table lists any PTIs issued or ROP revision applications received since the effective date of the previously issued ROP No. MI-ROP-N2388-2008a. Those ROP revision applications that are being issued concurrently with this ROP renewal are identified by an asterisk (\*). Those revision applications not listed with an asterisk were processed prior to this renewal.

Source-Wide PTI No MI-PTI-N2388-2008a is being reissued as Source-Wide PTI No. MI-PTI-N2388-2014.

|  |  |  |  |
| --- | --- | --- | --- |
| **Permit to Install Number** | **ROP Revision****Application Number** | **Description of Equipment or Change** | **Corresponding Emission Unit(s) or****Flexible Group(s)** |
| NA | 200900024 | Reopening to include requirements of the Clean Air Interstate Rule (CAIR) Annual Sulfur Dioxide Permit, CAIR Annual Nitrogen Oxide Budget Permit, and CAIR Ozone Nitrogen Oxide Budget Permit | EUBOILER |

The following ROP amendments or modifications were issued after the effective date of ROP No. MI-ROP-N2388-2014.

| **Permit to Install Number** | **ROP Revision Application Number/Issuance Date** | **Description of Change** | **Corresponding Emission Unit(s) or Flexible Group(s)** |
| --- | --- | --- | --- |
| NA | 201500158/June 16, 2016 | Reopening to update from CAIR to CSAPR. | FGCOMBTURB |

## Appendix 7. Emission Calculations

**Emission Calculations**

The permittee shall use the following calculations in conjunction with monitoring, testing or recordkeeping data to determine compliance with the applicable requirements referenced in EUBOILER.

For all pollutants **not** monitored by CEMS or COMS, the following formula shall be used to calculate emissions:

 Feed (calculated) X Emissions (test)\* = **Emissions (calculated)** Where:

 Feed (test)\*

Emissions (test) - is the final result of pollutant emissions in the appropriate units

(ie. #/MMBtu, lb/hr, ppmv, etc)

Feed (test) - is the feed rate achieved during testing

Feed (calculated) - is the feed rate achieved during the reporting period in question

\*value taken from the most recent valid stack testing data

All other specific emission calculations to be used with monitoring, testing or recordkeeping data are detailed in the appropriate Requirement Tables.

## Appendix 8. Reporting

**A. Annual, Semiannual, and Deviation Certification Reporting**

The permittee shall use the MDEQ, AQD, Report Certification form (EQP 5736) and MDEQ, AQD, Deviation Report form (EQP 5737) for the annual, semiannual and deviation certification reporting referenced in the Reporting Section of the Source-Wide, Emission Unit and/or Flexible Group Special Conditions. Alternative formats must meet the provisions of Rule 213(4)(c) and Rule 213(3)(c)(i), respectively, and be approved by the AQD District Supervisor.

**B. Other Reporting**

Specific reporting requirement formats and procedures are detailed in Part A or the appropriate Source-Wide, Emission Unit and/or Flexible Group Special Conditions. Therefore, Part B of this appendix is not applicable.

## Appendix 9. Transport Rule (TR) Trading Program Title V Requirements

**Description of TR Monitoring Provisions**

The TR subject unit, and the unit-specific monitoring provisions, at this source is identified in the following table. This unit is subject to the requirements for the TR NOX Annual Trading Program, TR NOX Ozone Season Trading Program, and TR SO2 Group 1 Trading Program, which are included below as Sections I, II, and III, respectively.

Each unit will use one of the following as the monitoring methodology for each parameter as provided below and shall comply with the general monitoring, recordkeeping, reporting and other requirements in conditions 1 through 5 below and in paragraph (b) of Sections I, II, and III:

* Continuous emission monitoring system or systems (CEMS) requirements pursuant to 40 CFR part 75, subpart B (for SO2 monitoring) and 40 CFR part 75, subpart H (for NOX monitoring)
* Excepted monitoring system requirements for gas- and oil-fired units pursuant to 40 CFR part 75, appendix D
* Excepted monitoring system requirements for gas- and oil-fired peaking units pursuant to 40 CFR part 75, appendix E
* Low Mass Emissions excepted monitoring (LME) requirements for gas- and oil-fired units pursuant to 40 CFR 75.19
* EPA-approved alternative monitoring system requirements pursuant to 40 CFR part 75, subpart E

|  |
| --- |
| Unit ID: 1 |
| Parameter | Monitoring Methodology |
| SO2 | Continuous emission monitoring system or systems (CEMS) requirements pursuant to 40 CFR part 75, subpart B  |
| NOx | Continuous emission monitoring system or systems (CEMS) requirements pursuant to 40 CFR part 75, subpart H  |
| Heat Input | Continuous emission monitoring system or systems (CEMS) requirements pursuant to 40 CFR part 75, subpart B (for SO2 monitoring) and 40 CFR part 75, subpart H (for NOX monitoring) |

1. The above description of the monitoring used by a unit does not change, create an exemption from, or otherwise affect the monitoring, recordkeeping, and reporting requirements applicable to the unit under 40 CFR 97.430 through 97.435 (TR NOX Annual Trading Program), 97.530 through 97.535 (TR NOX Ozone Season Trading Program), and 97.630 through 97.635 (TR SO2 Group 1 Trading Program). The monitoring, recordkeeping and reporting requirements applicable to each unit are included below in the standard conditions for the applicable TR trading programs.

2. Owners and operators must submit to the Administrator a monitoring plan for each unit in accordance with 40 CFR 75.53, 75.62 and 75.73, as applicable. The monitoring plan for each unit is available at the EPA’s website at <http://www.epa.gov/airmarkets/emissions/monitoringplans.html>.

3. Owners and operators that want to use an alternative monitoring system must submit to the Administrator a petition requesting approval of the alternative monitoring system in accordance with 40 CFR part 75, subpart E and 40 CFR 75.66 and 97.435 (TR NOX Annual Trading Program), 97.535 (TR NOX Ozone Season Trading Program), and/or 97.635 (TR SO2 Group 1 Trading Program). The Administrator’s response approving or disapproving any petition for an alternative monitoring system is available on the EPA’s website at <http://www.epa.gov/airmarkets/emissions/petitions.html>.

4. Owners and operators that want to use an alternative to any monitoring, recordkeeping, or reporting requirement under 40 CFR 97.430 through 97.434 (TR NOX Annual Trading Program), 97.530 through 97.534 (TR NOX Ozone Season Trading Program), and/or 97.630 through 97.634 (TR SO2 Group 1 Trading Program) must submit to the Administrator a petition requesting approval of the alternative in accordance with 40 CFR 75.66 and 97.435 (TR NOX Annual Trading Program), 97.535 (TR NOX Ozone Season Trading Program), and/or 97.635 (TR SO2 Group 1 Trading Program). The Administrator’s response approving or disapproving any petition for an alternative to a monitoring, recordkeeping, or reporting requirement is available on the EPA’s website at <http://www.epa.gov/airmarkets/emissions/petitions.html>.

5. The descriptions of monitoring applicable to the unit included above meet the requirement of 40 CFR 97.430 through 97.434 (TR NOX Annual Trading Program), 97.530 through 97.534 (TR NOX Ozone Season Trading Program), and 97.630 through 97.634 (TR SO2 Group 1 Trading Program), and therefore minor permit modification procedures, in accordance with 40 CFR 70.7(e)(2)(i)(B) or 71.7(e)(1)(i)(B), may be used to add or change this unit’s monitoring system description.

**SECTION I: TR NOX Annual Trading Program requirements (40 CFR 97.406)**

1. **Designated representative requirements.**

The owners and operators shall comply with the requirement to have a designated representative, and may have an alternate designated representative, in accordance with 40 CFR 97.413 through 97.418.

1. **Emissions monitoring, reporting, and recordkeeping requirements.**
2. The owners and operators, and the designated representative, of each TR NOX Annual source and each TR NOX Annual unit at the source shall comply with the monitoring, reporting, and recordkeeping requirements of 40 CFR 97.430 (general requirements, including installation, certification, and data accounting, compliance deadlines, reporting data, prohibitions, and long-term cold storage), 97.431 (initial monitoring system certification and recertification procedures), 97.432 (monitoring system out-of-control periods), 97.433 (notifications concerning monitoring), 97.434 (recordkeeping and reporting, including monitoring plans, certification applications, quarterly reports, and compliance certification), and 97.435 (petitions for alternatives to monitoring, recordkeeping, or reporting requirements).
3. The emissions data determined in accordance with 40 CFR 97.430 through 97.435 shall be used to calculate allocations of TR NOX Annual allowances under 40 CFR 97.411(a)(2) and (b) and 97.412 and to determine compliance with the TR NOX Annual emissions limitation and assurance provisions under paragraph (c) below, provided that, for each monitoring location from which mass emissions are reported, the mass emissions amount used in calculating such allocations and determining such compliance shall be the mass emissions amount for the monitoring location determined in accordance with 40 CFR 97.430 through 97.435 and rounded to the nearest ton, with any fraction of a ton less than 0.50 being deemed to be zero.
4. **NOX emissions requirements.**
5. TR NOX Annual emissions limitation.
	1. As of the allowance transfer deadline for a control period in a given year, the owners and operators of each TR NOX Annual source and each TR NOX Annual unit at the source shall hold, in the source's compliance account, TR NOX Annual allowances available for deduction for such control period under 40 CFR 97.424(a) in an amount not less than the tons of total NOX emissions for such control period from all TR NOX Annual units at the source.
	2. If total NOX emissions during a control period in a given year from the TR NOX Annual units at a TR NOX Annual source are in excess of the TR NOX Annual emissions limitation set forth in paragraph (c)(1)(i) above, then:
		1. The owners and operators of the source and each TR NOX Annual unit at the source shall hold the TR NOX Annual allowances required for deduction under 40 CFR 97.424(d); and
		2. The owners and operators of the source and each TR NOX Annual unit at the source shall pay any fine, penalty, or assessment or comply with any other remedy imposed, for the same violations, under the Clean Air Act, and each ton of such excess emissions and each day of such control period shall constitute a separate violation of 40 CFR part 97, subpart AAAAA and the Clean Air Act.
6. TR NOX Annual assurance provisions.
	1. If total NOX emissions during a control period in a given year from all TR NOX Annual units at TR NOX Annual sources in the state and Indian country within the borders of such State exceed the state assurance level, then the owners and operators of such sources and units in each group of one or more sources and units having a common designated representative for such control period, where the common designated representative’s share of such NOX emissions during such control period exceeds the common designated representative’s assurance level for the state and such control period, shall hold (in the assurance account established for the owners and operators of such group) TR NOX Annual allowances available for deduction for such control period under 40 CFR 97.425(a) in an amount equal to two times the product (rounded to the nearest whole number), as determined by the Administrator in accordance with 40 CFR 97.425(b), of multiplying— (A) The quotient of the amount by which the common designated representative’s share of such NOX emissions exceeds the common designated representative’s assurance level divided by the sum of the amounts, determined for all common designated representatives for such sources and units in the state and Indian country within the borders of such statefor such control period, by which each common designated representative’s share of such NOX emissions exceeds the respective common designated representative’s assurance level; and (B) The amount by which total NOX emissions from all TR NOX Annual units at TR NOX Annual sources in the state and Indian country within the borders of such statefor such control period exceed the state assurance level.
	2. The owners and operators shall hold the TR NOX Annual allowances required under paragraph (c)(2)(i) above, as of midnight of November 1 (if it is a business day), or midnight of the first business day thereafter (if November 1 is not a business day), immediately after such control period.
	3. Total NOX emissions from all TR NOX Annual units at TR NOX Annual sources in the State and Indian country within the borders of such stateduring a control period in a given year exceed the state assurance level if such total NOX emissions exceed the sum, for such control period, of the state NOX Annual trading budget under 40 CFR 97.410(a) and the state’s variability limit under 40 CFR 97.410(b).
	4. It shall not be a violation of 40 CFR part 97, subpart AAAAA or of the Clean Air Act if total NOX emissions from all TR NOX Annual units at TR NOX Annual sources in the State and Indian country within the borders of such State during a control period exceed the state assurance level or if a common designated representative’s share of total NOXemissions from the TR NOX Annual units at TR NOX Annual sources in the state and Indian country within the borders of such stateduring a control period exceeds the common designated representative’s assurance level.
	5. To the extent the owners and operators fail to hold TR NOX Annual allowances for a control period in a given year in accordance with paragraphs (c)(2)(i) through (iii) above,
		1. The owners and operators shall pay any fine, penalty, or assessment or comply with any other remedy imposed under the Clean Air Act; and
		2. Each TR NOX Annual allowance that the owners and operators fail to hold for such control period in accordance with paragraphs (c)(2)(i) through (iii) above and each day of such control period shall constitute a separate violation of 40 CFR part 97, subpart AAAAA and the Clean Air Act.
7. Compliance periods.
	1. A TR NOX Annual unit shall be subject to the requirements under paragraph (c)(1) above for the control period starting on the later of January 1, 2015, or the deadline for meeting the unit's monitor certification requirements under 40 CFR 97.430(b) and for each control period thereafter.
	2. A TR NOX Annual unit shall be subject to the requirements under paragraph (c)(2) above for the control period starting on the later of January 1, 2017 or the deadline for meeting the unit's monitor certification requirements under 40 CFR 97.430(b) and for each control period thereafter.
8. Vintage of allowances held for compliance.
	1. A TR NOX Annual allowance held for compliance with the requirements under paragraph (c)(1)(i) above for a control period in a given year must be a TR NOX Annual allowance that was allocated for such control period or a control period in a prior year.
	2. A TR NOX Annual allowance held for compliance with the requirements under paragraphs (c)(1)(ii)(A) and (2)(i) through (iii) above for a control period in a given year must be a TR NOX Annual allowance that was allocated for a control period in a prior year or the control period in the given year or in the immediately following year.
9. Allowance Management System requirements. Each TR NOX Annual allowance shall be held in, deducted from, or transferred into, out of, or between Allowance Management System accounts in accordance with 40 CFR part 97, subpart AAAAA.
10. Limited authorization. A TR NOX Annual allowance is a limited authorization to emit one ton of NOX during the control period in one year. Such authorization is limited in its use and duration as follows:
	1. Such authorization shall only be used in accordance with the TR NOX Annual Trading Program; and
	2. Notwithstanding any other provision of 40 CFR part 97, the Administrator has the authority to terminate or limit the use and duration of such authorization to the extent the Administrator determines is necessary or appropriate to implement any provision of the Clean Air Act.
11. Property right. A TR NOX Annual allowance does not constitute a property right.
12. **Title V permit revision requirements.**
	1. No title V permit revision shall be required for any allocation, holding, deduction, or transfer of TR NOX Annual allowances in accordance with 40 CFR part 97, subpart AAAAA.
	2. This permit incorporates the TR emissions monitoring, recordkeeping and reporting requirements pursuant to 40 CFR 97.430 through 97.435, and the requirements for a continuous emission monitoring system (pursuant to 40 CFR part 75, subparts B and H), an excepted monitoring system (pursuant to 40 CFR part 75, appendices D and E), a low mass emissions excepted monitoring methodology (pursuant to 40 CFR 75.19), and an alternative monitoring system (pursuant to 40 CFR part 75, subpart E). Therefore, the Description of TR Monitoring Provisions table for units identified in this permit may be added to, or changed, in this title V permit using minor permit modification procedures in accordance with 40 CFR 97.406(d)(2) and 70.7(e)(2)(i)(B) or 71.7(e)(1)(i)(B).
13. **Additional recordkeeping and reporting requirements.**
14. Unless otherwise provided, the owners and operators of each TR NOX Annual source and each TR NOX Annual unit at the source shall keep on site at the source each of the following documents (in hardcopy or electronic format) for a period of 5 years from the date the document is created. This period may be extended for cause, at any time before the end of 5 years, in writing by the Administrator.
	1. The certificate of representation under 40 CFR 97.416 for the designated representative for the source and each TR NOX Annual unit at the source and all documents that demonstrate the truth of the statements in the certificate of representation; provided that the certificate and documents shall be retained on site at the source beyond such 5-year period until such certificate of representation and documents are superseded because of the submission of a new certificate of representation under 40 CFR 97.416 changing the designated representative.
	2. All emissions monitoring information, in accordance with 40 CFR part 97, subpart AAAAA.
	3. Copies of all reports, compliance certifications, and other submissions and all records made or required under, or to demonstrate compliance with the requirements of, the TR NOX Annual Trading Program.
15. The designated representative of a TR NOX Annual source and each TR NOX Annual unit at the source shall make all submissions required under the TR NOX Annual Trading Program, except as provided in 40 CFR 97.418. This requirement does not change, create an exemption from, or otherwise affect the responsible official submission requirements under a title V operating permit program in 40 CFR parts 70 and 71.
16. **Liability*.***
	1. Any provision of the TR NOX Annual Trading Program that applies to a TR NOX Annual source or the designated representative of a TR NOX Annual source shall also apply to the owners and operators of such source and of the TR NOX Annual units at the source.
	2. Any provision of the TR NOX Annual Trading Program that applies to a TR NOX Annual unit or the designated representative of a TR NOX Annual unit shall also apply to the owners and operators of such unit.
17. **Effect on other authorities*.***

No provision of the TR NOX Annual Trading Program or exemption under 40 CFR 97.405 shall be construed as exempting or excluding the owners and operators, and the designated representative, of a TR NOX Annual source or TR NOX Annual unit from compliance with any other provision of the applicable, approved state implementation plan, a federally enforceable permit, or the Clean Air Act.

1. **Effect on units in Indian country.**

Notwithstanding the provisions of paragraphs (a) through (g) above, paragraphs (a) through (g) shall be deemed not to impose any requirements on any source or unit, or any owner, operator, or designated representative with regard to any source or unit, in Indian country within the borders of the state.

**SECTION II: TR NOX Ozone Season Trading Program Requirements (40 CFR 97.506)**

1. **Designated representative requirements.**

The owners and operators shall comply with the requirement to have a designated representative, and may have an alternate designated representative, in accordance with 40 CFR 97.513 through 97.518.

1. **Emissions monitoring, reporting, and recordkeeping requirements.**
2. The owners and operators, and the designated representative, of each TR NOX Ozone Season source and each TR NOX Ozone Season unit at the source shall comply with the monitoring, reporting, and recordkeeping requirements of 40 CFR 97.530 (general requirements, including installation, certification, and data accounting, compliance deadlines, reporting data, prohibitions, and long-term cold storage), 97.531 (initial monitoring system certification and recertification procedures), 97.532 (monitoring system out-of-control periods), 97.533 (notifications concerning monitoring), 97.534 (recordkeeping and reporting, including monitoring plans, certification applications, quarterly reports, and compliance certification), and 97.535 (petitions for alternatives to monitoring, recordkeeping, or reporting requirements).
3. The emissions data determined in accordance with 40 CFR 97.530 through 97.535 shall be used to calculate allocations of TR NOX Ozone Season allowances under 40 CFR 97.511(a)(2) and (b) and 97.512 and to determine compliance with the TR NOX Ozone Season emissions limitation and assurance provisions under paragraph (c) below, provided that, for each monitoring location from which mass emissions are reported, the mass emissions amount used in calculating such allocations and determining such compliance shall be the mass emissions amount for the monitoring location determined in accordance with 40 CFR 97.530 through 97.535 and rounded to the nearest ton, with any fraction of a ton less than 0.50 being deemed to be zero.
4. **NOX emissions requirements.**
5. TR NOX Ozone Season emissions limitation.
	1. As of the allowance transfer deadline for a control period in a given year, the owners and operators of each TR NOX Ozone Season source and each TR NOX Ozone Season unit at the source shall hold, in the source's compliance account, TR NOX Ozone Season allowances available for deduction for such control period under 40 CFR 97.524(a) in an amount not less than the tons of total NOX emissions for such control period from all TR NOX Ozone Season units at the source.
	2. If total NOX emissions during a control period in a given year from the TR NOX Ozone Season units at a TR NOX Ozone Season source are in excess of the TR NOX Ozone Season emissions limitation set forth in paragraph (c)(1)(i) above, then:
		1. The owners and operators of the source and each TR NOX Ozone Season unit at the source shall hold the TR NOX Ozone Season allowances required for deduction under 40 CFR 97.524(d); and
		2. The owners and operators of the source and each TR NOX Ozone Season unit at the source shall pay any fine, penalty, or assessment or comply with any other remedy imposed, for the same violations, under the Clean Air Act, and each ton of such excess emissions and each day of such control period shall constitute a separate violation of 40 CFR part 97, subpart BBBBB and the Clean Air Act.
6. TR NOX Ozone Season assurance provisions.
	1. If total NOX emissions during a control period in a given year from all TR NOX Ozone Season units at TR NOX Ozone Season sources in the state and Indian country within the borders of such stateexceed the state assurance level, then the owners and operators of such sources and units in each group of one or more sources and units having a common designated representative for such control period, where the common designated representative’s share of such NOX emissions during such control period exceeds the common designated representative’s assurance level for the state and such control period, shall hold (in the assurance account established for the owners and operators of such group) TR NOX Ozone Season allowances available for deduction for such control period under 40 CFR 97.525(a) in an amount equal to two times the product (rounded to the nearest whole number), as determined by the Administrator in accordance with 40 CFR 97.525(b), of multiplying—
		1. The quotient of the amount by which the common designated representative’s share of such NOX emissions exceeds the common designated representative’s assurance level divided by the sum of the amounts, determined for all common designated representatives for such sources and units in the state and Indian country within the borders of such statefor such control period, by which each common designated representative’s share of such NOX emissions exceeds the respective common designated representative’s assurance level; and
		2. The amount by which total NOX emissions from all TR NOX Ozone Season units at TR NOX Ozone Season sources in the state and Indian country within the borders of such statefor such control period exceed the state assurance level.
	2. The owners and operators shall hold the TR NOX Ozone Season allowances required under paragraph (c)(2)(i) above, as of midnight of November 1 (if it is a business day), or midnight of the first business day thereafter (if November 1 is not a business day), immediately after such control period.
	3. Total NOX emissions from all TR NOX Ozone Season units at TR NOX Ozone Season sources in the state and Indian country within the borders of such stateduring a control period in a given year exceed the state assurance level if such total NOX emissions exceed the sum, for such control period, of the State NOX Ozone Season trading budget under 40 CFR 97.510(a) and the state’s variability limit under 40 CFR 97.510(b).
	4. It shall not be a violation of 40 CFR part 97, subpart BBBBB or of the Clean Air Act if total NOX emissions from all TR NOX Ozone Season units at TR NOX Ozone Season sources in the state and Indian country within the borders of such stateduring a control period exceed the state assurance level or if a common designated representative’s share of total NOX emissions from the TR NOX Ozone Season units at TR NOX Ozone Season sources in the state and Indian country within the borders of such stateduring a control period exceeds the common designated representative’s assurance level.
	5. To the extent the owners and operators fail to hold TR NOX Ozone Season allowances for a control period in a given year in accordance with paragraphs (c)(2)(i) through (iii) above,
		1. The owners and operators shall pay any fine, penalty, or assessment or comply with any other remedy imposed under the Clean Air Act; and
		2. Each TR NOX Ozone Season allowance that the owners and operators fail to hold for such control period in accordance with paragraphs (c)(2)(i) through (iii) above and each day of such control period shall constitute a separate violation of 40 CFR part 97, subpart BBBBB and the Clean Air Act.
7. Compliance periods.
	1. A TR NOX Ozone Season unit shall be subject to the requirements under paragraph (c)(1) above for the control period starting on the later of May 1, 2015 or the deadline for meeting the unit's monitor certification requirements under 40 CFR 97.530(b) and for each control period thereafter.
	2. A TR NOX Ozone Season unit shall be subject to the requirements under paragraph (c)(2) above for the control period starting on the later of May 1, 2017 or the deadline for meeting the unit's monitor certification requirements under 40 CFR 97.530(b) and for each control period thereafter.
8. Vintage of allowances held for compliance.
	1. A TR NOX Ozone Season allowance held for compliance with the requirements under paragraph (c)(1)(i) above for a control period in a given year must be a TR NOX Ozone Season allowance that was allocated for such control period or a control period in a prior year.
	2. A TR NOX Ozone Season allowance held for compliance with the requirements under paragraphs (c)(1)(ii)(A) and (2)(i) through (iii) above for a control period in a given year must be a TR NOX Ozone Season allowance that was allocated for a control period in a prior year or the control period in the given year or in the immediately following year.
9. Allowance Management System requirements. Each TR NOX Ozone Season allowance shall be held in, deducted from, or transferred into, out of, or between Allowance Management System accounts in accordance with 40 CFR part 97, subpart BBBBB.
10. Limited authorization. A TR NOX Ozone Season allowance is a limited authorization to emit one ton of NOX during the control period in one year. Such authorization is limited in its use and duration as follows:
	1. Such authorization shall only be used in accordance with the TR NOX Ozone Season Trading Program; and
	2. Notwithstanding any other provision of 40 CFR part 97, subpart BBBBB, the Administrator has the authority to terminate or limit the use and duration of such authorization to the extent the Administrator determines is necessary or appropriate to implement any provision of the Clean Air Act.
11. Property right. A TR NOX Ozone Season allowance does not constitute a property right.
12. **Title V permit revision requirements*.***
13. No title V permit revision shall be required for any allocation, holding, deduction, or transfer of TR NOX Ozone Season allowances in accordance with 40 CFR part 97, subpart BBBBB.
14. This permit incorporates the TR emissions monitoring, recordkeeping and reporting requirements pursuant to 40 CFR 97.530 through 97.535, and the requirements for a continuous emission monitoring system (pursuant to 40 CFR part 75, subparts B and H), an excepted monitoring system (pursuant to 40 CFR part 75, appendices D and E), a low mass emissions excepted monitoring methodology (pursuant to 40 CFR 75.19), and an alternative monitoring system (pursuant to 40 CFR part 75, subpart E). Therefore, the Description of TR Monitoring Provisions table for units identified in this permit may be added to, or changed, in this title V permit using minor permit modification procedures in accordance with 40 CFR 97.506(d)(2) and 70.7(e)(2)(i)(B) or 71.7(e)(1)(i)(B).
15. **Additional recordkeeping and reporting requirements*.***
16. Unless otherwise provided, the owners and operators of each TR NOX Ozone Season source and each TR NOX Ozone Season unit at the source shall keep on site at the source each of the following documents (in hardcopy or electronic format) for a period of 5 years from the date the document is created. This period may be extended for cause, at any time before the end of 5 years, in writing by the Administrator.
	1. The certificate of representation under 40 CFR 97.516 for the designated representative for the source and each TR NOX Ozone Season unit at the source and all documents that demonstrate the truth of the statements in the certificate of representation; provided that the certificate and documents shall be retained on site at the source beyond such 5-year period until such certificate of representation and documents are superseded because of the submission of a new certificate of representation under 40 CFR 97.516 changing the designated representative.
	2. All emissions monitoring information, in accordance with 40 CFR part 97, subpart BBBBB.
	3. Copies of all reports, compliance certifications, and other submissions and all records made or required under, or to demonstrate compliance with the requirements of, the TR NOX Ozone Season Trading Program.
17. The designated representative of a TR NOX Ozone Season source and each TR NOX Ozone Season unit at the source shall make all submissions required under the TR NOX Ozone Season Trading Program, except as provided in 40 CFR 97.518. This requirement does not change, create an exemption from, or otherwise affect the responsible official submission requirements under a title V operating permit program in 40 CFR parts 70 and 71.
18. **Liability*.***
19. Any provision of the TR NOX Ozone Season Trading Program that applies to a TR NOX Ozone Season source or the designated representative of a TR NOX Ozone Season source shall also apply to the owners and operators of such source and of the TR NOX Ozone Season units at the source.
20. Any provision of the TR NOX Ozone Season Trading Program that applies to a TR NOX Ozone Season unit or the designated representative of a TR NOX Ozone Season unit shall also apply to the owners and operators of such unit.
21. **Effect on other authorities*.***

No provision of the TR NOX Ozone Season Trading Program or exemption under 40 CFR 97.505 shall be construed as exempting or excluding the owners and operators, and the designated representative, of a TR NOX Ozone Season source or TR NOX Ozone Season unit from compliance with any other provision of the applicable, approved state implementation plan, a federally enforceable permit, or the Clean Air Act.

1. **Effect on units in Indian country.**

Notwithstanding the provisions of paragraphs (a) through (g) above, paragraphs (a) through (g) shall be deemed not to impose any requirements on any source or unit, or any owner, operator, or designated representative with regard to any source or unit, in Indian country within the borders of the state.

**SECTION III: TR SO2 Group 1 Trading Program requirements (40 CFR 97.606)**

1. **Designated representative requirements.**

The owners and operators shall comply with the requirement to have a designated representative, and may have an alternate designated representative, in accordance with 40 CFR 97.613 through 97.618.

1. **Emissions monitoring, reporting, and recordkeeping requirements.**
2. The owners and operators, and the designated representative, of each TR SO2 Group 1 source and each TR SO2 Group 1 unit at the source shall comply with the monitoring, reporting, and recordkeeping requirements of 40 CFR 97.630 (general requirements, including installation, certification, and data accounting, compliance deadlines, reporting data, prohibitions, and long-term cold storage), 97.631 (initial monitoring system certification and recertification procedures), 97.632 (monitoring system out-of-control periods), 97.633 (notifications concerning monitoring), 97.634 (recordkeeping and reporting, including monitoring plans, certification applications, quarterly reports, and compliance certification), and 97.635 (petitions for alternatives to monitoring, recordkeeping, or reporting requirements).
3. The emissions data determined in accordance with 40 CFR 97.630 through 97.635 shall be used to calculate allocations of TR SO2 Group 1 allowances under 40 CFR 97.611(a)(2) and (b) and 97.612 and to determine compliance with the TR SO2 Group 1 emissions limitation and assurance provisions under paragraph (c) below, provided that, for each monitoring location from which mass emissions are reported, the mass emissions amount used in calculating such allocations and determining such compliance shall be the mass emissions amount for the monitoring location determined in accordance with 40 CFR 97.630 through 97.635 and rounded to the nearest ton, with any fraction of a ton less than 0.50 being deemed to be zero.
4. **SO2 emissions requirements.**
5. TR SO2 Group 1 emissions limitation.
	1. As of the allowance transfer deadline for a control period in a given year, the owners and operators of each TR SO2 Group 1 source and each TR SO2 Group 1 unit at the source shall hold, in the source's compliance account, TR SO2 Group 1 allowances available for deduction for such control period under 40 CFR 97.624(a) in an amount not less than the tons of total SO2 emissions for such control period from all TR SO2 Group 1 units at the source.
	2. If total SO2 emissions during a control period in a given year from the TR SO2 Group 1 units at a TR SO2 Group 1 source are in excess of the TR SO2 Group 1 emissions limitation set forth in paragraph (c)(1)(i) above, then:
		1. The owners and operators of the source and each TR SO2 Group 1 unit at the source shall hold the TR SO2 Group 1 allowances required for deduction under 40 CFR 97.624(d); and
		2. The owners and operators of the source and each TR SO2 Group 1 unit at the source shall pay any fine, penalty, or assessment or comply with any other remedy imposed, for the same violations, under the Clean Air Act, and each ton of such excess emissions and each day of such control period shall constitute a separate violation 40 CFR part 97, subpart CCCCC and the Clean Air Act.
6. TR SO2 Group 1 assurance provisions.
	1. If total SO2 emissions during a control period in a given year from all TR SO2 Group 1 units at TR SO2 Group 1 sources in the state and Indian country within the borders of such state exceed the state assurance level, then the owners and operators of such sources and units in each group of one or more sources and units having a common designated representative for such control period, where the common designated representative’s share of such SO2 emissions during such control period exceeds the common designated representative’s assurance level for the state and such control period, shall hold (in the assurance account established for the owners and operators of such group) TR SO2 Group 1 allowances available for deduction for such control period under 40 CFR 97.625(a) in an amount equal to two times the product (rounded to the nearest whole number), as determined by the Administrator in accordance with 40 CFR 97.625(b), of multiplying—
		1. The quotient of the amount by which the common designated representative’s share of such SO2 emissions exceeds the common designated representative’s assurance level divided by the sum of the amounts, determined for all common designated representatives for such sources and units in the state and Indian country within the borders of such statefor such control period, by which each common designated representative’s share of such SO2 emissions exceeds the respective common designated representative’s assurance level; and
		2. The amount by which total SO2 emissions from all TR SO2 Group 1 units at TR SO2 Group 1 sources in the state and Indian country within the borders of such statefor such control period exceed the state assurance level.
	2. The owners and operators shall hold the TR SO2 Group 1 allowances required under paragraph (c)(2)(i) above, as of midnight of November 1 (if it is a business day), or midnight of the first business day thereafter (if November 1 is not a business day), immediately after such control period.
	3. Total SO2 emissions from all TR SO2 Group 1 units at TR SO2 Group 1 sources in the state and Indian country within the borders of such state during a control period in a given year exceed the state assurance level if such total SO2 emissions exceed the sum, for such control period, of the state SO2 Group 1 trading budget under 40 CFR 97.610(a) and the state’s variability limit under 40 CFR 97.610(b).
	4. It shall not be a violation of 40 CFR part 97, subpart CCCCC or of the Clean Air Act if total SO2 emissions from all TR SO2 Group 1 units at TR SO2 Group 1 sources in the state and Indian country within the borders of such stateduring a control period exceed the state assurance level or if a common designated representative’s share of total SO2 emissions from the TR SO2 Group 1 units at TR SO2 Group 1 sources in the state and Indian country within the borders of such state during a control period exceeds the common designated representative’s assurance level.
	5. To the extent the owners and operators fail to hold TR SO2 Group 1 allowances for a control period in a given year in accordance with paragraphs (c)(2)(i) through (iii) above,
		1. The owners and operators shall pay any fine, penalty, or assessment or comply with any other remedy imposed under the Clean Air Act; and
		2. Each TR SO2 Group 1 allowance that the owners and operators fail to hold for such control period in accordance with paragraphs (c)(2)(i) through (iii) above and each day of such control period shall constitute a separate violation of 40 CFR part 97, subpart CCCCC and the Clean Air Act.
7. Compliance periods.
	1. A TR SO2 Group 1 unit shall be subject to the requirements under paragraph (c)(1) above for the control period starting on the later of January 1, 2015 or the deadline for meeting the unit's monitor certification requirements under 40 CFR 97.630(b) and for each control period thereafter.
	2. A TR SO2 Group 1 unit shall be subject to the requirements under paragraph (c)(2) above for the control period starting on the later of January 1, 2017 or the deadline for meeting the unit's monitor certification requirements under 40 CFR 97.630(b) and for each control period thereafter.
8. Vintage of allowances held for compliance.
	1. A TR SO2 Group 1 allowance held for compliance with the requirements under paragraph (c)(1)(i) above for a control period in a given year must be a TR SO2 Group 1 allowance that was allocated for such control period or a control period in a prior year.
	2. A TR SO2 Group 1 allowance held for compliance with the requirements under paragraphs (c)(1)(ii)(A) and (2)(i) through (iii) above for a control period in a given year must be a TR SO2 Group 1 allowance that was allocated for a control period in a prior year or the control period in the given year or in the immediately following year.
9. Allowance Management System requirements. Each TR SO2 Group 1 allowance shall be held in, deducted from, or transferred into, out of, or between Allowance Management System accounts in accordance with 40 CFR part 97, subpart CCCCC.
10. Limited authorization. A TR SO2 Group 1 allowance is a limited authorization to emit one ton of SO2 during the control period in one year. Such authorization is limited in its use and duration as follows:
	1. Such authorization shall only be used in accordance with the TR SO2 Group 1 Trading Program; and
	2. Notwithstanding any other provision of 40 CFR part 97, subpart CCCCC, the Administrator has the authority to terminate or limit the use and duration of such authorization to the extent the Administrator determines is necessary or appropriate to implement any provision of the Clean Air Act.
11. Property right. A TR SO2 Group 1 allowance does not constitute a property right.
12. **Title V permit revision requirements.**
13. No title V permit revision shall be required for any allocation, holding, deduction, or transfer of TR SO2 Group 1 allowances in accordance with 40 CFR part 97, subpart CCCCC.
14. This permit incorporates the TR emissions monitoring, recordkeeping and reporting requirements pursuant to 40 CFR 97.630 through 97.635, and the requirements for a continuous emission monitoring system (pursuant to 40 CFR part 75, subparts B and H), an excepted monitoring system (pursuant to 40 CFR part 75, appendices D and E), a low mass emissions excepted monitoring methodology (pursuant to 40 CFR part 75.19), and an alternative monitoring system (pursuant to 40 CFR part 75, subpart E), Therefore, the Description of TR Monitoring Provisions table for units identified in this permit may be added to, or changed, in this title V permit using minor permit modification procedures in accordance with 40 CFR 97.606(d)(2) and 70.7(e)(2)(i)(B) or 71.7(e)(1)(i)(B).
15. **Additional recordkeeping and reporting requirements.**
16. Unless otherwise provided, the owners and operators of each TR SO2 Group 1 source and each TR SO2 Group 1 unit at the source shall keep on site at the source each of the following documents (in hardcopy or electronic format) for a period of 5 years from the date the document is created. This period may be extended for cause, at any time before the end of 5 years, in writing by the Administrator.
	1. The certificate of representation under 40 CFR 97.616 for the designated representative for the source and each TR SO2 Group 1 unit at the source and all documents that demonstrate the truth of the statements in the certificate of representation; provided that the certificate and documents shall be retained on site at the source beyond such 5-year period until such certificate of representation and documents are superseded because of the submission of a new certificate of representation under 40 CFR 97.616 changing the designated representative.
	2. All emissions monitoring information, in accordance with 40 CFR part 97, subpart CCCCC.
	3. Copies of all reports, compliance certifications, and other submissions and all records made or required under, or to demonstrate compliance with the requirements of, the TR SO2 Group 1 Trading Program.
17. The designated representative of a TR SO2 Group 1 source and each TR SO2 Group 1 unit at the source shall make all submissions required under the TR SO2 Group 1 Trading Program, except as provided in 40 CFR 97.618. This requirement does not change, create an exemption from, or otherwise affect the responsible official submission requirements under a title V operating permit program in 40 CFR parts 70 and 71.
18. **Liability.**
19. Any provision of the TR SO2 Group 1 Trading Program that applies to a TR SO2 Group 1 source or the designated representative of a TR SO2 Group 1 source shall also apply to the owners and operators of such source and of the TR SO2 Group 1 units at the source.
20. Any provision of the TR SO2 Group 1 Trading Program that applies to a TR SO2 Group 1 unit or the designated representative of a TR SO2 Group 1 unit shall also apply to the owners and operators of such unit.
21. **Effect on other authorities.**

No provision of the TR SO2 Group 1 Trading Program or exemption under 40 CFR 97.605 shall be construed as exempting or excluding the owners and operators, and the designated representative, of a TR SO2 Group 1 source or TR SO2 Group 1 unit from compliance with any other provision of the applicable, approved state implementation plan, a federally enforceable permit, or the Clean Air Act.

**(h) Effect on units in Indian country.**

Notwithstanding the provisions of paragraphs (a) through (g) above, paragraphs (a) through (g) shall be deemed not to impose any requirements on any source or unit, or any owner, operator, or designated representative with regard to any source or unit, in Indian country within the borders of the state.