|  |  |  |
| --- | --- | --- |
|  | **MICHIGAN DEPARTMENT OF ENVIRONMENTAL QUALITY**  **AIR QUALITY DIVISION** |  |
| EFFECTIVE DATE: April 23, 2019  ISSUED TO  **Sturgis Municipal Power Plant**  State Registration Number (SRN): B7287  LOCATED AT  505 West Chicago Road, Sturgis, Michigan 49091 | | |
|  | | |
| **RENEWABLE OPERATING PERMIT**  Permit Number: MI-ROP-B7287-2019  Expiration Date: April 23, 2024  Administratively Complete ROP Renewal Application Due Between  October 23, 2022 and October 23, 2023  This Renewable Operating Permit (ROP) is issued in accordance with and subject to Section 5506(3) of Part 55, Air Pollution Control, of the Natural Resources and Environmental Protection Act, 1994 PA 451, as amended (Act 451). Pursuant to Rule 210(1) of the administrative rules promulgated under Act 451, this ROP constitutes the permittee’s authority to operate the stationary source identified above in accordance with the general conditions, special conditions and attachments contained herein. Operation of the stationary source and all emission units listed in the permit are subject to all applicable future or amended rules and regulations pursuant to Act 451 and the federal Clean Air Act. | | |

|  |
| --- |
| **SOURCE-WIDE PERMIT TO INSTALL**  Permit Number: MI-PTI-B7287-2019  This Permit to Install (PTI) is issued in accordance with and subject to Section 5505(1) of Act 451. Pursuant to Rule 214a of the administrative rules promulgated under Act 451, the terms and conditions herein, identified by the underlying applicable requirement citation of Rule 201(1)(a), constitute a federally enforceable PTI. The PTl terms and conditions do not expire and remain in effect unless the criteria of Rule 201(6) are met. Operation of all emission units identified in the PTI is subject to all applicable future or amended rules and regulations pursuant to Act 451 and the federal Clean Air Act. |

Michigan Department of Environmental Quality

Rex Lane, Kalamazoo District Supervisor **TABLE OF CONTENTS**

[AUTHORITY AND ENFORCEABILITY 3](#_Toc775689)

[A. GENERAL CONDITIONS 4](#_Toc775690)

[Permit Enforceability 4](#_Toc775691)

[General Provisions 4](#_Toc775692)

[Equipment & Design 5](#_Toc775693)

[Emission Limits 5](#_Toc775694)

[Testing/Sampling 5](#_Toc775695)

[Monitoring/Recordkeeping 6](#_Toc775696)

[Certification & Reporting 6](#_Toc775697)

[Permit Shield 7](#_Toc775698)

[Revisions 8](#_Toc775699)

[Reopenings 8](#_Toc775700)

[Renewals 8](#_Toc775701)

[Stratospheric Ozone Protection 9](#_Toc775702)

[Risk Management Plan 9](#_Toc775703)

[Emission Trading 9](#_Toc775704)

[Permit to Install (PTI) 9](#_Toc775705)

[B. SOURCE-WIDE CONDITIONS 11](#_Toc775706)

[C. EMISSION UNIT SPECIAL CONDITIONS 12](#_Toc775707)

[EMISSION UNIT SUMMARY TABLE 12](#_Toc775708)

[EU-ENG-6 13](#_Toc775709)

[EU-OIL-TANK 19](#_Toc775710)

[D. FLEXIBLE GROUP SPECIAL CONDITIONS 21](#_Toc775711)

[FLEXIBLE GROUP SUMMARY TABLE 21](#_Toc775712)

[FG-COLDCLEANERS 22](#_Toc775713)

[E. NON-APPLICABLE REQUIREMENTS 25](#_Toc775714)

[APPENDICES 26](#_Toc775715)

[Appendix 1. Acronyms and Abbreviations 26](#_Toc775716)

[Appendix 2. Schedule of Compliance 27](#_Toc775717)

[Appendix 3. Monitoring Requirements 27](#_Toc775718)

[Appendix 4. Recordkeeping 27](#_Toc775719)

[Appendix 5. Testing Procedures 27](#_Toc775720)

[Appendix 6. Permits to Install 27](#_Toc775721)

[Appendix 7. Emission Calculations 27](#_Toc775722)

[Appendix 8. Reporting 27](#_Toc775723)

# AUTHORITY AND ENFORCEABILITY

For the purpose of this permit, the **permittee** is defined as any person who owns or operates an emission unit at a stationary source for which this permit has been issued. The **department** is defined in Rule 104(d) as the Director of the Michigan Department of Environmental Quality (MDEQ) or his or her designee.

The permittee shall comply with all specific details in the permit terms and conditions and the cited underlying applicable requirements. All terms and conditions in this ROP are both federally enforceable and state enforceable unless otherwise footnoted. Certain terms and conditions are applicable to most stationary sources for which an ROP has been issued. These general conditions are included in Part A of this ROP. Other terms and conditions may apply to a specific emission unit, several emission units which are represented as a flexible group, or the entire stationary source which is represented as a Source-Wide group. Special conditions are identified in Parts B, C, D and/or the appendices.

In accordance with Rule 213(2)(a), all underlying applicable requirements are identified for each ROP term or condition. All terms and conditions that are included in a PTI are streamlined, subsumed and/or is state-only enforceable will be noted as such.

In accordance with Section 5507 of Act 451, the permittee has included in the ROP application a compliance certification, a schedule of compliance, and a compliance plan. For applicable requirements with which the source is in compliance, the source will continue to comply with these requirements. For applicable requirements with which the source is not in compliance, the source will comply with the detailed schedule of compliance requirements that are incorporated as an appendix in this ROP. Furthermore, for any applicable requirements effective after the date of issuance of this ROP, the stationary source will meet the requirements on a timely basis, unless the underlying applicable requirement requires a more detailed schedule of compliance.

Issuance of this permit does not obviate the necessity of obtaining such permits or approvals from other units of government as required by law.

# A. GENERAL CONDITIONS

## Permit Enforceability

* All conditions in this permit are both federally enforceable and state enforceable unless otherwise noted. **(R 336.1213(5))**
* Those conditions that are hereby incorporated in a state-only enforceable Source-Wide PTI pursuant to Rule 201(2)(d) are designated by footnote one. **(R 336.1213(5)(a), R 336.1214a(5))**
* Those conditions that are hereby incorporated in a federally enforceable Source-Wide PTI pursuant to Rule 201(2)(c) are designated by footnote two. **(R 336.1213(5)(b), R 336.1214a(3))**

## General Provisions

1. The permittee shall comply with all conditions of this ROP. Any ROP noncompliance constitutes a violation of Act 451, and is grounds for enforcement action, for ROP revocation or revision, or for denial of the renewal of the ROP. All terms and conditions of this ROP that are designated as federally enforceable are enforceable by the Administrator of the United States Environmental Protection Agency (USEPA) and by citizens under the provisions of the federal Clean Air Act (CAA). Any terms and conditions based on applicable requirements which are designated as “state-only” are not enforceable by the USEPA or citizens pursuant to the CAA. **(R 336.1213(1)(a))**
2. It shall not be a defense for the permittee in an enforcement action that it would have been necessary to halt or reduce the permitted activity in order to maintain compliance with the conditions of this ROP. **(R 336.1213(1)(b))**
3. This ROP may be modified, revised, or revoked for cause. The filing of a request by the permittee for a permit modification, revision, or termination, or a notification of planned changes or anticipated noncompliance does not stay any ROP term or condition. This does not supersede or affect the ability of the permittee to make changes, at the permittee’s own risk, pursuant to Rule 215 and Rule 216. **(R 336.1213(1)(c))**
4. The permittee shall allow the department, or an authorized representative of the department, upon presentation of credentials and other documents as may be required by law and upon stating the authority for and purpose of the investigation, to perform any of the following activities: **(R 336.1213(1)(d))**
   1. Enter, at reasonable times, a stationary source or other premises where emissions-related activity is conducted or where records must be kept under the conditions of the ROP.
   2. Have access to and copy, at reasonable times, any records that must be kept under the conditions of the ROP.
   3. Inspect, at reasonable times, any of the following:
      1. Any stationary source.
      2. Any emission unit.
      3. Any equipment, including monitoring and air pollution control equipment.
      4. Any work practices or operations regulated or required under the ROP.
   4. As authorized by Section 5526 of Act 451, sample or monitor at reasonable times substances or parameters for the purpose of assuring compliance with the ROP or applicable requirements.
5. The permittee shall furnish to the department, within a reasonable time, any information the department may request, in writing, to determine whether cause exists for modifying, revising, or revoking the ROP or to determine compliance with this ROP. Upon request, the permittee shall also furnish to the department copies of any records that are required to be kept as a term or condition of this ROP. For information which is claimed by the permittee to be confidential, consistent with the requirements of the 1976 PA 442, MCL §15.231 et seq., and known as the Freedom of Information Act, the person may also be required to furnish the records directly to the USEPA together with a claim of confidentiality. **(R 336.1213(1)(e))**
6. A challenge by any person, the Administrator of the USEPA, or the department to a particular condition or a part of this ROP shall not set aside, delay, stay, or in any way affect the applicability or enforceability of any other condition or part of this ROP. **(R 336.1213(1)(f))**
7. The permittee shall pay fees consistent with the fee schedule and requirements pursuant to Section 5522 of Act 451. **(R 336.1213(1)(g))**
8. This ROP does not convey any property rights or any exclusive privilege. **(R 336.1213(1)(h))**

## Equipment & Design

1. Any collected air contaminants shall be removed as necessary to maintain the equipment at the required operating efficiency. The collection and disposal of air contaminants shall be performed in a manner so as to minimize the introduction of contaminants to the outer air. Transport of collected air contaminants in Priority I and II areas requires the use of material handling methods specified in Rule 370(2).2 **(R 336.1370)**
2. Any air cleaning device shall be installed, maintained, and operated in a satisfactory manner and in accordance with the Michigan Air Pollution Control rules and existing law. **(R 336.1910)**

## Emission Limits

1. Unless otherwise specified in this ROP, the permittee shall comply with Rule 301, which states, in part, “Except as provided in Subrules 2, 3, and 4 of this rule, a person shall not cause or permit to be discharged into the outer air from a process or process equipment a visible emission of a density greater than the most stringent of the following:”2 **(R 336.1301(1))**
   1. A 6-minute average of 20% opacity, except for one 6-minute average per hour of not more than 27% opacity.
   2. A limit specified by an applicable federal new source performance standard.

The grading of visible emissions shall be determined in accordance with Rule 303.

1. The permittee shall not cause or permit the emission of an air contaminant or water vapor in quantities that cause, alone or in reaction with other air contaminants, either of the following:
   1. Injurious effects to human health or safety, animal life, plant life of significant economic value, or property.1 **(R 336.1901(a))**
   2. Unreasonable interference with the comfortable enjoyment of life and property.1**(R 336.1901(b))**

## Testing/Sampling

1. The department may require the owner or operator of any source of an air contaminant to conduct acceptable performance tests, at the owner’s or operator’s expense, in accordance with Rule 1001 and Rule 1003, under any of the conditions listed in Rule 1001(1).2 **(R 336.2001)**
2. Any required performance testing shall be conducted in accordance with Rule 1001(2), Rule 1001(3) and Rule 1003. **(R 336.2001(2), R 336.2001(3), R 336.2003(1))**
3. Any required test results shall be submitted to the Air Quality Division (AQD) in the format prescribed by the applicable reference test method within 60 days following the last date of the test. **(R 336.2001(5))**

## Monitoring/Recordkeeping

1. Records of any periodic emission or parametric monitoring required in this ROP shall include the following information specified in Rule 213(3)(b)(i), where appropriate: **(R 336.1213(3)(b))**
   1. The date, location, time, and method of sampling or measurements.
   2. The dates the analyses of the samples were performed.
   3. The company or entity that performed the analyses of the samples.
   4. The analytical techniques or methods used.
   5. The results of the analyses.
   6. The related process operating conditions or parameters that existed at the time of sampling or measurement.
2. All required monitoring data, support information and all reports, including reports of all instances of deviation from permit requirements, shall be kept and furnished to the department upon request for a period of not less than 5 years from the date of the monitoring sample, measurement, report or application. Support information includes all calibration and maintenance records and all original strip-chart recordings, or other original data records, for continuous monitoring instrumentation and copies of all reports required by the ROP. **(R 336.1213(1)(e), R 336.1213(3)(b)(ii))**

## Certification & Reporting

1. Except for the alternate certification schedule provided in Rule 213(3)(c)(iii)(B), any document required to be submitted to the department as a term or condition of this ROP shall contain an original certification by a Responsible Official which states that, based on information and belief formed after reasonable inquiry, the statements and information in the document are true, accurate, and complete. **(R 336.1213(3)(c))**
2. A Responsible Official shall certify to the appropriate AQD District Office and to the USEPA that the stationary source is and has been in compliance with all terms and conditions contained in the ROP except for deviations that have been or are being reported to the appropriate AQD District Office pursuant to Rule 213(3)(c). This certification shall include all the information specified in Rule 213(4)(c)(i) through (v) and shall state that, based on information and belief formed after reasonable inquiry, the statements and information in the certification are true, accurate, and complete. The USEPA address is: USEPA, Air Compliance Data - Michigan, Air and Radiation Division, 77 West Jackson Boulevard, Chicago, Illinois 60604-3507. **(R 336.1213(4)(c))**
3. The certification of compliance shall be submitted annually for the term of this ROP as detailed in the special conditions, or more frequently if specified in an applicable requirement or in this ROP. **(R 336.1213(4)(c))**
4. The permittee shall promptly report any deviations from ROP requirements and certify the reports. The prompt reporting of deviations from ROP requirements is defined in Rule 213(3)(c)(ii) as follows, unless otherwise described in this ROP: **(R 336.1213(3)(c))**
   1. For deviations that exceed the emissions allowed under the ROP, prompt reporting means reporting consistent with the requirements of Rule 912 as detailed in Condition 25. All reports submitted pursuant to this paragraph shall be promptly certified as specified in Rule 213(3)(c)(iii).
   2. For deviations which exceed the emissions allowed under the ROP and which are not reported pursuant to Rule 912 due to the duration of the deviation, prompt reporting means the reporting of all deviations in the semiannual reports required by Rule 213(3)(c)(i). The report shall describe reasons for each deviation and the actions taken to minimize or correct each deviation.
   3. For deviations that do not exceed the emissions allowed under the ROP, prompt reporting means the reporting of all deviations in the semiannual reports required by Rule 213(3)(c)(i). The report shall describe the reasons for each deviation and the actions taken to minimize or correct each deviation.
5. For reports required pursuant to Rule 213(3)(c)(ii), prompt certification of the reports is described in Rule 213(3)(c)(iii) as either of the following: **(R 336.1213(3)(c))**
   1. Submitting a certification by a Responsible Official with each report which states that, based on information and belief formed after reasonable inquiry, the statements and information in the report are true, accurate, and complete.
   2. Submitting, within 30 days following the end of a calendar month during which one or more prompt reports of deviations from the emissions allowed under the ROP were submitted to the department pursuant to Rule 213(3)(c)(ii), a certification by a Responsible Official which states that; “based on information and belief formed after reasonable inquiry, the statements and information contained in each of the reports submitted during the previous month were true, accurate, and complete.” The certification shall include a listing of the reports that are being certified. Any report submitted pursuant to Rule 213(3)(c)(ii) that will be certified on a monthly basis pursuant to this paragraph shall include a statement that certification of the report will be provided within 30 days following the end of the calendar month.
6. Semiannually for the term of the ROP as detailed in the special conditions, or more frequently if specified, the permittee shall submit certified reports of any required monitoring to the appropriate AQD District Office. All instances of deviations from ROP requirements during the reporting period shall be clearly identified in the reports. **(R 336.1213(3)(c)(i))**
7. On an annual basis, the permittee shall report the actual emissions, or the information necessary to determine the actual emissions, of each regulated air pollutant as defined in Rule 212(6) for each emission unit utilizing the emissions inventory forms provided by the department. **(R 336.1212(6))**
8. The permittee shall provide notice of an abnormal condition, start-up, shutdown, or malfunction that results in emissions of a hazardous or toxic air pollutant which continue for more than one hour in excess of any applicable standard or limitation, or emissions of any air contaminant continuing for more than two hours in excess of an applicable standard or limitation, as required in Rule 912, to the appropriate AQD District Office. The notice shall be provided not later than two business days after the start-up, shutdown, or discovery of the abnormal conditions or malfunction. Notice shall be by any reasonable means, including electronic, telephonic, or oral communication. Written reports, if required under Rule 912, must be submitted to the appropriate AQD District Supervisor within 10 days after the start-up or shutdown occurred, within 10 days after the abnormal conditions or malfunction has been corrected, or within 30 days of discovery of the abnormal conditions or malfunction, whichever is first. The written reports shall include all of the information required in Rule 912(5) and shall be certified by a Responsible Official in a manner consistent with the CAA.2 **(R 336.1912)**

## Permit Shield

1. Compliance with the conditions of the ROP shall be considered compliance with any applicable requirements as of the date of ROP issuance if either of the following provisions is satisfied: **(R 336.1213(6)(a)(i), R 336.1213(6)(a)(ii))**
   1. The applicable requirements are included and are specifically identified in the ROP.
   2. The permit includes a determination or concise summary of the determination by the department that other specifically identified requirements are not applicable to the stationary source.

Any requirements identified in Part E of this ROP have been identified as non-applicable to this ROP and are included in the permit shield.

1. Nothing in this ROP shall alter or affect any of the following:
   1. The provisions of Section 303 of the CAA, emergency orders, including the authority of the USEPA under Section 303 of the CAA. **(R 336.1213(6)(b)(i))**
   2. The liability of the owner or operator of this source for any violation of applicable requirements prior to or at the time of this ROP issuance. **(R 336.1213(6)(b)(ii))**
   3. The applicable requirements of the acid rain program, consistent with Section 408(a) of the CAA. **(R 336.1213(6)(b)(iii))**
   4. The ability of the USEPA to obtain information from a source pursuant to Section 114 of the CAA. **(R 336.1213(6)(b)(iv))**
2. The permit shield shall not apply to provisions incorporated into this ROP through procedures for any of the following:
   1. Operational flexibility changes made pursuant to Rule 215. **(R 336.1215(5))**
   2. Administrative Amendments made pursuant to Rule 216(1)(a)(i)-(iv). **(R 336.1216(1)(b)(iii))**
   3. Administrative Amendments made pursuant to Rule 216(1)(a)(v) until the amendment has been approved by the department. **(R 336.1216(1)(c)(iii))**
   4. Minor Permit Modifications made pursuant to Rule 216(2). **(R 336.1216(2)(f))**
   5. State-Only Modifications made pursuant to Rule 216(4) until the changes have been approved by the department. **(R 336.1216(4)(e))**
3. Expiration of this ROP results in the loss of the permit shield. If a timely and administratively complete application for renewal is submitted not more than 18 months, but not less than 6 months, before the expiration date of the ROP, but the department fails to take final action before the end of the ROP term, the existing ROP does not expire until the renewal is issued or denied, and the permit shield shall extend beyond the original ROP term until the department takes final action. **(R 336.1217(1)(c), R 336.1217(1)(a))**

## Revisions

1. For changes to any process or process equipment covered by this ROP that do not require a revision of the ROP pursuant to Rule 216, the permittee must comply with Rule 215. **(R 336.1215, R 336.1216)**
2. A change in ownership or operational control of a stationary source covered by this ROP shall be made pursuant to Rule 216(1). **(R 336.1219(2))**
3. For revisions to this ROP, an administratively complete application shall be considered timely if it is received by the department in accordance with the time frames specified in Rule 216. **(R 336.1210(10))**
4. Pursuant to Rule 216(1)(b)(iii), Rule 216(2)(d) and Rule 216(4)(d), after a change has been made, and until the department takes final action, the permittee shall comply with both the applicable requirements governing the change and the ROP terms and conditions proposed in the application for the modification. During this time period, the permittee may choose to not comply with the existing ROP terms and conditions that the application seeks to change. However, if the permittee fails to comply with the ROP terms and conditions proposed in the application during this time period, the terms and conditions in the ROP are enforceable. **(R 336.1216(1)(c)(iii), R 336.1216(2)(d), R 336.1216(4)(d))**

## Reopenings

1. A ROP shall be reopened by the department prior to the expiration date and revised by the department under any of the following circumstances:
   1. If additional requirements become applicable to this stationary source with three or more years remaining in the term of the ROP, but not if the effective date of the new applicable requirement is later than the ROP expiration date. **(R 336.1217(2)(a)(i))**
   2. If additional requirements pursuant to Title IV of the CAA become applicable to this stationary source. **(R 336.1217(2)(a)(ii))**
   3. If the department determines that the ROP contains a material mistake, information required by any applicable requirement was omitted, or inaccurate statements were made in establishing emission limits or the terms or conditions of the ROP. **(R 336.1217(2)(a)(iii))**
   4. If the department determines that the ROP must be revised to ensure compliance with the applicable requirements. **(R 336.1217(2)(a)(iv))**

## Renewals

1. For renewal of this ROP, an administratively complete application shall be considered timely if it is received by the department not more than 18 months, but not less than 6 months, before the expiration date of the ROP. **(R 336.1210(9))**

## Stratospheric Ozone Protection

1. If the permittee is subject to Title 40 of the Code of Federal Regulations (CFR), Part 82 and services, maintains, or repairs appliances except for motor vehicle air conditioners (MVAC), or disposes of appliances containing refrigerant, including MVAC and small appliances, or if the permittee is a refrigerant reclaimer, appliance owner or a manufacturer of appliances or recycling and recovery equipment, the permittee shall comply with all applicable standards for recycling and emissions reduction pursuant to 40 CFR Part 82, Subpart F.
2. If the permittee is subject to 40 CFR Part 82 and performs a service on motor (fleet) vehicles when this service involves refrigerant in the MVAC, the permittee is subject to all the applicable requirements as specified in 40 CFR Part 82, Subpart B, Servicing of Motor Vehicle Air Conditioners. The term “motor vehicle” as used in Subpart B does not include a vehicle in which final assembly of the vehicle has not been completed by the original equipment manufacturer. The term MVAC as used in Subpart B does not include the air-tight sealed refrigeration system used for refrigerated cargo or an air conditioning system on passenger buses using Hydrochlorofluorocarbon-22 refrigerant.

## Risk Management Plan

1. If subject to Section 112(r) of the CAA and 40 CFR Part 68, the permittee shall register and submit to the USEPA the required data related to the risk management plan for reducing the probability of accidental releases of any regulated substances listed pursuant to Section 112(r)(3) of the CAA as amended in 40 CFR 68.130. The list of substances, threshold quantities, and accident prevention regulations promulgated under 40 CFR Part 68, do not limit in any way the general duty provisions under Section 112(r)(1).
2. If subject to Section 112(r) of the CAA and 40 CFR Part 68, the permittee shall comply with the requirements of 40 CFR Part 68, no later than the latest of the following dates as provided in 40 CFR 68.10(a):
   1. June 21, 1999,
   2. Three years after the date on which a regulated substance is first listed under 40 CFR 68.130, or
   3. The date on which a regulated substance is first present above a threshold quantity in a process.
3. If subject to Section 112(r) of the CAA and 40 CFR Part 68, the permittee shall submit any additional relevant information requested by any regulatory agency necessary to ensure compliance with the requirements of 40 CFR Part 68.
4. If subject to Section 112(r) of the CAA and 40 CFR Part 68, the permittee shall annually certify compliance with all applicable requirements of Section 112(r) as detailed in Rule 213(4)(c)). **(40 CFR Part 68)**

## Emission Trading

1. Emission averaging and emission reduction credit trading are allowed pursuant to any applicable interstate or regional emission trading program that has been approved by the Administrator of the USEPA as a part of Michigan’s State Implementation Plan. Such activities must comply with Rule 215 and Rule 216. **(R 336.1213(12))**

## Permit to Install (PTI)

1. The process or process equipment included in this permit shall not be reconstructed, relocated, or modified unless a PTI authorizing such action is issued by the department, except to the extent such action is exempt from the PTI requirements by any applicable rule.2 **(R 336.1201(1))**
2. The department may, after notice and opportunity for a hearing, revoke PTI terms or conditions if evidence indicates the process or process equipment is not performing in accordance with the terms and conditions of the PTI or is violating the department’s rules or the CAA.2 **(R 336.1201(8), Section 5510 of Act 451)**
3. The terms and conditions of a PTI shall apply to any person or legal entity that now or hereafter owns or operates the process or process equipment at the location authorized by the PTI. If a new owner or operator submits a written request to the department pursuant to Rule 219 and the department approves the request, this PTI will be amended to reflect the change of ownership or operational control. The request must include all of the information required by Subrules (1)(a), (b) and (c) of Rule 219. The written request shall be sent to the appropriate AQD District Supervisor, MDEQ.2**(R 336.1219)**
4. If the installation, reconstruction, relocation, or modification of the equipment for which PTI terms and conditions have been approved has not commenced within 18 months of the original PTI issuance date, or has been interrupted for 18 months, the applicable terms and conditions from that PTI, as incorporated into the ROP, shall become void unless otherwise authorized by the department. Furthermore, the person to whom that PTI was issued, or the designated authorized agent, shall notify the department via the Supervisor, Permit Section, MDEQ, AQD, P.O. Box 30260, Lansing, Michigan 48909, if it is decided not to pursue the installation, reconstruction, relocation, or modification of the equipment allowed by the terms and conditions from that PTI.2 **(R 336.1201(4))**

**Footnotes:**

1This condition is state-only enforceable and was established pursuant to Rule 201(1)(b).

2This condition is federally enforceable and was established pursuant to Rule 201(1)(a).

# B. SOURCE-WIDE CONDITIONS

Part B outlines the Source-Wide Terms and Conditions that apply to this stationary source. The permittee is subject to these special conditions for the stationary source in addition to the general conditions in Part A and any other terms and conditions contained in this ROP.

The permittee shall comply with all specific details in the special conditions and the underlying applicable requirements cited. If a specific condition type does not apply to this source, NA (not applicable) has been used in the table. If there are no Source-Wide Conditions, this section will be left blank.

# C. EMISSION UNIT SPECIAL CONDITIONS

Part C outlines terms and conditions that are specific to individual emission units listed in the Emission Unit Summary Table. The permittee is subject to the special conditions for each emission unit in addition to the General Conditions in Part A and any other terms and conditions contained in this ROP.

The permittee shall comply with all specific details in the special conditions and the underlying applicable requirements cited. If a specific condition type does not apply, NA (not applicable) has been used in the table. If there are no conditions specific to individual emission units, this section will be left blank.

## EMISSION UNIT SUMMARY TABLE

The descriptions provided below are for informational purposes and do not constitute enforceable conditions.

| **Emission Unit ID** | **Emission Unit Description**  **(Including Process Equipment & Control Device(s))** | **Installation**  **Date/**  **Modification Date** | **Flexible Group ID** |
| --- | --- | --- | --- |
| EU-ENG-6 | Dual fuel engine generator No. 6. fires No. 2 fuel oil and natural gas. Nameplate capacity is 8,285 HP engine with 6,000 KW generator. The engine uses non-contact cooling water. A diesel oxidation catalyst was installed to control CO as a result of RICE NESHAP regulations. Includes 40 CFR Part 60, Subpart ZZZZ, requirements. | 01-01-1981 | NA |
| EU-COLDCLEANERS | Cold cleaner(s). | 01-01-1995 | FG-COLDCLEANERS |
| EU-OIL-TANK | 30,000 gallon aboveground tank for storing No. 2 fuel oil. | 01-01-1995 | NA |

## EU-ENG-6

**EMISSION UNIT CONDITIONS**

**DESCRIPTION**

Dual fuel engine generator No. 6. fires No. 2 fuel oil and natural gas. Nameplate capacity is 8,285 HP engine with 6,000 KW generator. The engine uses non-contact cooling water. A diesel oxidation catalyst was installed to control CO as a result of RICE NESHAP regulations. Includes 40 CFR Part 60, Subpart ZZZZ, requirements.

**Flexible Group ID:** NA

**POLLUTION CONTROL EQUIPMENT**

Oxidation catalyst for control of carbon monoxide

**I. EMISSION LIMITS**

| **Pollutant** | **Limit** | **Time Period/ Operating Scenario** | **Equipment** | **Monitoring/**  **Testing Method** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- | --- | --- |
| 1. NOx | 12.9 grams/HP-hr2 | Average of three 1-hour or longer runs | EU-ENG-6 | SC V.2 | **R 336.1201(3)** |
| 1. CO | 23 ppmvd at 15% O2 or reduce CO emissions by 70% or more except during periods of startup | Average of three 1-hour or longer runs. | EU-ENG-6 | Method 10 of 40 CFR Part 60, Appendix A or other approved method, SC V.3 | **40 CFR 63.6603(a)** |

**II. MATERIAL LIMIT**

| **Material** | **Limit** | **Time Period/ Operating Scenario** | **Equipment** | **Monitoring/**  **Testing Method** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- | --- | --- |
| 1. No. 2 Fuel Oil | 0.5% Sulfur2\* | Calculated on the basis of 19,460 BTUs/pound | EU-ENG-6 | SC V.1 and VI.7 | **R 336.1201(3)** |

\*In accordance with Rule 213(2) and Rule 213(6), compliance with this streamlined material limit shall be considered compliance with the material limit established by R 336.1201(3); and also compliance with the material limit established by R 336.1401(1), an additional applicable requirement that has been subsumed within this condition.

**III. PROCESS/OPERATIONAL RESTRICTIONS**

1. The maximum sulfur content in the No. 2 fuel oil shall not exceed the equivalent of 0.5%, calculated on the basis of 19,460 BTUs per pound. Compliance with this condition shall be considered compliance with the following applicable requirement that has been subsumed under this streamlined requirement: R 336.1401(1).2 **(R 336.1201(3))**
2. EU-ENG-6 shall not be used to generate more than 13.1 million KW-hr (17.5 million HP-hr) of electricity per year.2 **(R 336.1205(3))**
3. The permittee shall operate and maintain EU-ENG-6, including associated air pollution control equipment and monitoring equipment, in a manner consistent with safety and good air pollution control practices for minimizing emissions. The general duty to minimize emissions does not require the permittee to make further effort to reduce emissions if levels required by this permit have been achieved. Determination of whether such operation and maintenance procedures are being used will be based on information available to the AQD which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source. **(40 CFR 63.6605(b))**
4. The permittee shall be in compliance with the emission limitations, operating limitations, and other requirements of 40 CFR Part 63, Subpart ZZZZ that apply at all times. **(40 CFR 63.6605(a))**
5. The permittee shall maintain the catalyst so that the pressure drop across the catalyst does not change by more than 2 inches of water from the pressure drop across the catalyst that was measured during the initial performance test except during periods of startup. **(40 CFR 63.6630(b))**
6. The permittee shall maintain the temperature of the stationary RICE exhaust so that the catalyst inlet temperature is greater than or equal to 4500 F and less than or equal to 13500  F except during periods of startup. **(40 CFR 63.6630(b))**
7. The permittee shall minimize the engine’s time spent at idle and minimize the engine’s startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the non-startup emission limitations apply. **(40 CFR 63.6603(a), 40 CFR 63.6625(h))**

**IV. DESIGN/EQUIPMENT PARAMETERS**

1. The permittee shall install, operate, and maintain a continuous parameter monitoring system (CPMS) in continuous operation according to the procedures in the site-specific monitoring plan. This shall include a CPMS for catalyst inlet temperature and catalyst pressure drop. **(40 CFR 63.6625(b)(2))**
2. The permittee shall prepare a site-specific monitoring plan that addresses the monitoring system design, data collection, and the quality assurance and quality control elements outlined in 40 CFR 63.6625(b)(1) through 40 CFR 63.6625(b)(5) and in 40 CFR 63.8(d). These elements shall consist of the following: **(40 CFR 63.6625(b)(1))**
   1. The performance criteria and design specifications for the monitoring system equipment, including the sample interface, detector signal analyzer, and data acquisition and calculations. **(40 CFR 63.6625(b)(1)(i))**
   2. Sampling interface (e.g. thermocouple) location such that the monitoring system will provide representative measurements. **(40 CFR 63.6625(b)(1)(ii))**
   3. Equipment performance evaluations, system accuracy audits, or other audit procedures. **(40 CFR 63.6625(b)(1)(iii))**
   4. Ongoing operation and maintenance procedures in accordance with provisions in 40 CFR 63.8(c)(1)(ii) and (c)(3). **(40 CFR 63.6625(b)(1)(iv))**

e. Ongoing reporting and recordkeeping procedures in accordance with provisions in 40 CFR 63.10(c), (e)(1), and (e)(2)(i). **(40 CFR 63.6625(b)(1)(v))**

3. The permittee shall conduct a performance evaluation of each CPMS in accordance with the site-specific monitoring plan. **(40 CFR 63.6625(b)(6))**

4. The CPMS shall collect data at least once every 15 minutes. **(40 CFR 63.6625(b)(3))**

5. For a CPMS for measuring temperature range, the temperature sensor must have a minimum tolerance of 2.8 degrees Celsius (5 degrees Fahrenheit) or 1 percent of the measurement range, whichever is larger. **(40 CFR 63.6625(b)(4))**

6. The permittee shall conduct the CPMS equipment performance evaluation, system accuracy audits, or other audit procedures specified in the site-specific monitoring plan at least annually. **(40 CFR 63.6625(b)(5))**

**V. TESTING/SAMPLING**

Records shall be maintained on file for a period of five years. **(R 336.1213(3)(b)(ii))**

1. Testing for percent sulfur content in No. 2 fuel oil shall be performed on an annual basis when fuel oil shipments have been received by the permittee during the calendar year. ASTM D129-64, ASTM D1552-83, ASTM D2622- 87, ASTM D1266-87, or an approved equivalent test method shall be used. The oil sample shall be collected from EU-OIL-TANK. **(R 336.1213(3))**

1. The permittee shall verify nitrogen oxides emission rates from EU-ENG-6 by testing at the owner’s expense once during the term of this permit, in accordance with the Department requirements. Testing shall be performed using an approved EPA Method listed in 40 CFR Part 60 Appendix A, Method 7. An alternate method, or a modification to the approved EPA Method, may be specified in an AQD‑approved Test Protocol. Testing shall be performed when EU-ENG-6 is firing No.2 fuel oil. No less than 30 days prior to testing, the permittee shall submit a complete test plan to the AQD Technical Programs Unit and District Office. The AQD must approve the final plan prior to testing, including any modifications to the method in the test protocol that are proposed after initial submittal. The permittee must submit a complete report of the test results to the AQD Technical Programs Unit and District Office within 60 days following the last date of the test.  **(R 336.1213(3), R 336.2001, R 336.2003, R 336.2004)**
2. The permittee shall verify carbon monoxide emission rates from EU-ENG-6 every 8,760 operating hours or three years, whichever comes first, by testing at owner's expense, in accordance with 40 CFR 63.6620. Testing shall be performed using an approved EPA Method listed in 40 CFR Part 63, Subpart ZZZZ, Table 4. Testing shall be performed separately with No. 2 fuel oil and with natural gas. Either of the two CO limits (23 ppmvd at 15% O2 or 70% reduction) may be chosen for each mode of fuel use. An alternate method, or a modification to the approved EPA Method, may be specified in an AQD-approved Test Protocol. No less than 60 days prior to testing, the permittee shall submit a complete test plan to the AQD Technical Programs Unit and District Office. The AQD must approve the final plan prior to testing, including any modifications to the method in the test protocol that are proposed after initial submittal. The permittee must submit a complete report of the test results to the AQD Technical Programs Unit and District Office within 60 days following the last date of the test. **(R 336.1213(3), R 336.2001, R 336.2003, R 336.2004, 40 CFR 63.6620, 40 CFR 63.6645(g))**
3. The permittee shall notify the AQD Technical Programs Unit Supervisor and the District Supervisor not less than 30 days of the time and place before performance tests are conducted. **(R 336.1213(3))**

**VI. MONITORING/RECORDKEEPING**

Records shall be maintained on file for a period of five years. **(R 336.1213(3)(b)(ii))**

1. The permittee shall maintain records of the amount of electricity produced by EU-ENG-6, in KW-hr, on a monthly basis. **(R 336.1213(3))**

2. The permittee shall maintain records of the amount of electricity produced by EU-ENG-6, in KW-hr, based on a 12-month rolling time period as determined at the end of each calendar month. **(R 336.1213(3))**

1. The permittee shall monitor and record the natural gas consumption rate, in cubic feet or million cubic feet, for EU-ENG-6 on a monthly basis. **(R 336.1213(3))**
2. The permittee shall monitor and record the natural gas consumption rate, in cubic feet or million cubic feet, for EU-ENG-6 based on a 12-month rolling time period as determined at the end of each calendar month. **(R 336.1213(3))**
3. The permittee shall monitor and record the No. 2 fuel oil consumption rate, in gallons, for EU-ENG-6 on a monthly basis. **(R 336.1213(3))**
4. The permittee shall monitor and record the No. 2 fuel oil consumption rate, in gallons, for EU-ENG-6 based on a 12-month rolling time period as determined at the end of each calendar month. **(R 336.1213(3))**
5. The permittee shall maintain records of No. 2 fuel oil specifications and/or a fuel oil analysis for each delivery to demonstrate compliance with the percent sulfur limit. **(R 336.1213(3))**
6. The permittee shall measure the pressure drop across the catalyst once per month and demonstrate that the pressure drop is within the operating limitation established during the performance test. **(40 CFR 63.6625(b))**
7. Except for monitor malfunctions, associated repairs, required performance evaluations, and required quality assurance or control activities, the permittee shall monitor continuously at all times that the stationary RICE is operating. A monitoring malfunction is any sudden, infrequent, not reasonably preventable failure of the monitoring to provide valid data. Monitoring failures that are caused in part by poor maintenance or careless operation are not malfunctions. **(40 CFR 63.6635(b))**
8. The permittee shall not use data recorded during monitoring malfunctions, associated repairs, and required quality assurance or control activities in data averages and calculations used to report emission or operating levels. The permittee shall use, however, all the valid data collected during all other periods. **(40 CFR 63.6635(c))**
9. The permittee shall collect catalyst inlet temperature data, reduce these data to 4-hour rolling averages and maintain the 4-hour rolling averages within the operating limitations for the catalyst inlet temperature. **(40 CFR 63.6625(b))**
10. If the permittee changes the catalyst, the permittee shall reestablish the values of the operating parameters measured during the initial performance test. When the values of the operating parameters are reestablished, the permittee shall also conduct a performance test to demonstrate that the required emission limitation is being met. **(40 CFR 63.6640(b))**
11. The permittee shall keep the following records as they apply to 40 CFR Part 63, Subpart ZZZZ:
    1. A copy of each notification and report that was submitted, including all documentation supporting any Initial Notification or Notification of Compliance Status that was submitted. **(40 CFR 63.6655(a)(1))**
    2. Records of the occurrence and duration of each malfunction of operation ( i.e., process equipment) or the air pollution control and monitoring equipment. **(40 CFR 63.6655(a)(2))**
    3. Records of performance tests and performance evaluations as required in 40 CFR 63.10(b)(2)(viii). **(40 CFR 63.6655(a)(3))**
    4. Records of all required maintenance performed on the air pollution control and monitoring equipment. **(40 CFR 63.6655(a)(4))**
    5. Records of actions taken during periods of malfunction to minimize emissions in accordance with 40 CFR 63.6605(b), including corrective actions to restore malfunctioning process and air pollution control and monitoring equipment to its normal or usual manner of operation. **(40 CFR 63.6655(a)(5))**
    6. For each CPMS:

i. Records described in 40 CFR 63.10(b)(2)(vi) through (xi). **(40 CFR 63.6655(b)(1))**

ii. Previous (i.e., superseded) versions of the performance evaluation plan as required in 40 CFR 63.8(d)(3). **(40 CFR 63.6655(b)(2))**

iii. Requests for alternatives to the relative accuracy test for CPMS as required in 40 CFR 63.8(f)(6)(i), if applicable. **(40 CFR 63.6655(b)(3))**

1. If the permittee does not operate EU-ENG-6 during a month it is not necessary to operate the unit for the sole purpose of measuring pressure drop across the catalyst as stated in SC VI.8. above. **(R 336.1213(3)(c)(iii))**

**VII. REPORTING**

1. Prompt reporting of deviations pursuant to General Conditions 21 and 22 of Part A. **(R 336.1213(3)(c)(ii))**

2. Semiannual reporting of monitoring and deviations pursuant to General Condition 23 of Part A. The report shall be postmarked orreceived by the appropriate AQD District Office by March 15 for reporting period July 1 to December 31 and September 15 for reporting period January 1 to June 30. **(R 336.1213(3)(c)(i))**

3. Annual certification of compliance pursuant to General Conditions 19 and 20 of Part A. The report shall be postmarked or received by the appropriate AQD District Office by March 15 for the previous calendar year. **(R 336.1213(4)(c))**

1. The permittee shall submit any performance test reports to the AQD Technical Programs Unit and District Office, in a format approved by the AQD. **(R 336.1213(3)(c), R 336.2001(5))**

5. The permittee shall submit all semiannual compliance reports as required by 40 CFR 63.6650(a). Each semiannual compliance shall cover the semiannual reporting period from January 1 through June 30 or the semiannual reporting period from July 1 through December 31. Each semiannual compliance report must be postmarked or delivered no later than July 31 or January 31, whichever date is the first date following the end of the semiannual reporting period. **(40 CFR 63.6650(a), 40 CFR 63.6650(b)(3), 40 CFR 63.6650(b)(4))**

6. The compliance report required in (5.) above shall contain the following information:

a. Company name and address. **(40 CFR 63.6650(c)(1))**

b. Statement by a responsible official with that official’s name, title, and signature, certifying the accuracy of the content of the report. **(40 CFR 63.6650(c)(2))**

c. Date of report and beginning and ending dates of the reporting period. **(40 CFR 63.6650(c)(3))**

d. The number, duration, and a brief description for each type of malfunction which occurred during the reporting period and which caused or may have caused any applicable emission limitation to be exceeded. The report shall also include a description of actions taken by an owner or operator during a malfunction of an affected source to minimize emissions in accordance with 40 CFR 63.6605(b), including actions to correct a malfunction. **(40 CFR 63.6650(c)(4))**

e. If there were no deviations from any emission or operating limitations, a statement that there were no deviations from the emission or operating limitations during the reporting period. **(40 CFR 63.6650(c)(5))**

f. If there were no periods during which the CPMS was out-of-control as specified in 40 CFR 63.8(c)(7), a statement that there were no periods during which the CPMS was out-of-control during the reporting period. **(40 CFR 63.6650(c)(6))**

7. For each deviation from an emission or operating limitation that occurs, the report required in (5,) above shall contain the following information:

a. The date and time that each malfunction started and stopped. **(40 CFR 63.6650(e)(1))**

b. The date, time, and duration that each CPMS was inoperative, except for zero (low-level and high-level checks. **(40 CFR 63.6650(e)(2))**

c. The date, time, and duration that each CPMS was out-of-control, including the information in 40 CFR 63.8(c)(8). **(40 CFR 63.6650(e)(3))**

d. The date and time that each deviation started and stopped, and whether each deviation occurred during a period of malfunction or during another period. **(40 CFR 63.6650(e)(4))**

e. A summary of the total duration of the deviation during the reporting period, and the total duration as a percent of the total source operating time during that reporting period. **(40 CFR 63.6650(e)(5))**

f. A breakdown of the total duration of the deviations during the reporting period into those that are due to control equipment problems, process problems, other known causes, and other unknown causes. **(40 CFR 63.6650(e)(6))**

g. A summary of the total duration of CPMS downtime during the reporting period, and the total duration of CPMS downtime as a percent of the total operating time of the stationary RICE at which the CPMS downtime occurred during the reporting period. **(40 CFR 6650(e)(7))**

h. An identification of each parameter and pollutant (CO) that was monitored at the stationary RICE. **(40 CFR 63.6650(e)(8))**

i. A brief description of the stationary RICE. **(40 CFR 63.6650(e)(9))**

j. A brief description of the CPMS. **(40 CFR 63.6650(e)(10))**

k. The date of the latest CPMS certification or audit. **(40 CFR 63.6650(e)(11))**

l. A description of any changes in CPMS, processes, or controls since the last reporting period. **(40 CFR 63.6650(e)(12))**

**See Appendix 8**

**VIII. STACK/VENT RESTRICTIONS**

The exhaust gases from the stacks listed in the table below shall be discharged unobstructed vertically upwards to the ambient air unless otherwise noted:

| **Stack & Vent ID** | **Maximum Exhaust Diameter / Dimensions**  **(inches)** | **Minimum Height Above Ground**  **(feet)** | **Underlying Applicable Requirements** |
| --- | --- | --- | --- |
| 1. SV-ENG-6 | 302 | 332 | **40 CFR 52.21** |

**IX. OTHER REQUIREMENTS**

1. The permittee shall comply with all applicable provisions of the National Emission Standards for Hazardous Air Pollutants, as specified in 40 CFR Part 63, Subpart A and Subpart ZZZZ for Stationary Reciprocating Internal Combustion Engines by the initial compliance date. **(40 CFR Part 63, Subparts A and ZZZZ)**

**Footnotes:**

1 This condition is state only enforceable and was established pursuant to Rule 201(1)(b).

2 This condition is federally enforceable and was established pursuant to Rule 201(1)(a).

## EU-OIL-TANK

**EMISSION UNIT CONDITIONS**

**DESCRIPTION**

30,000 gallon aboveground tank for storing No. 2 fuel oil.

**Flexible Group ID:** NA

**POLLUTION CONTROL EQUIPMENT**

NA

**I. EMISSION LIMIT(S)**

NA

**II. MATERIAL LIMIT(S)**

NA

**III. PROCESS/OPERATIONAL RESTRICTION(S)**

NA

**IV. DESIGN/EQUIPMENT PARAMETER(S)**

NA

**V. TESTING/SAMPLING**

Records shall be maintained on file for a period of five years. **(R 336.1213(3)(b)(ii))**

NA

**VI. MONITORING/RECORDKEEPING**

Records shall be maintained on file for a period of five years. **(R 336.1213(3)(b)(ii))**

1. The facility shall keep readily accessible records showing the dimensions and capacity of EU-OIL-TANK. **(40 CFR Part 60, Subpart Kb)**

**VII. REPORTING**

1. Prompt reporting of deviations pursuant to General Conditions 21 and 22 of Part A. **(R 336.1213(3)(c)(ii))**

2. Semiannual reporting of monitoring and deviations pursuant to General Condition 23 of Part A. The report shall be postmarked orreceived by the appropriate AQD District Office by March 15 for reporting period July 1 to December 31 and September 15 for reporting period January 1 to June 30. **(R 336.1213(3)(c)(i))**

3. Annual certification of compliance pursuant to General Conditions 19 and 20 of Part A. The report shall be postmarked or received by the appropriate AQD District Office by March 15 for the previous calendar year. **(R 336.1213(4)(c))**

**See Appendix 8**

**VIII. STACK/VENT RESTRICTION(S)**

NA

**IX. OTHER REQUIREMENT(S)**

NA

**Footnotes:**

1 This condition is state only enforceable and was established pursuant to Rule 201(1)(b).

2 This condition is federally enforceable and was established pursuant to Rule 201(1)(a).

# D. FLEXIBLE GROUP SPECIAL CONDITIONS

Part D outlines the terms and conditions that apply to more than one emission unit. The permittee is subject to the special conditions for each flexible group in addition to the General Conditions in Part A and any other terms and conditions contained in this ROP.

The permittee shall comply with all specific details in the special conditions and the underlying applicable requirements cited. If a specific condition type does not apply, NA has been used in the table. If there are no special conditions that apply to more than one emission unit, this section will be left blank.

## FLEXIBLE GROUP SUMMARY TABLE

The descriptions provided below are for informational purposes and do not constitute enforceable conditions.

| **Flexible Group ID** | **Flexible Group Description** | **Associated**  **Emission Unit IDs** |
| --- | --- | --- |
| FG-COLDCLEANERS | Any cold cleaner that is grandfathered or exempt from Rule 201 pursuant to Rule 278, Rule 278a and Rule 281(2)(h) or Rule 285(2)(r)(iv). Existing cold cleaners were placed into operation prior to July 1, 1979. New cold cleaners were placed into operation on or after July 1, 1979. | EU-COLDCLEANERS |

## FG-COLDCLEANERS

**FLEXIBLE GROUP CONDITIONS**

**DESCRIPTION**

Any cold cleaner that is grandfathered or exempt from Rule 201 pursuant to Rule 278, Rule 278a and Rule 281(2)(h) or Rule 285(2)(r)(iv). Existing cold cleaners were placed into operation prior to July 1, 1979. New cold cleaners were placed into operation on or after July 1, 1979.

**Emission Unit:** EU-COLDCLEANERS

**POLLUTION CONTROL EQUIPMENT**

NA

**I. EMISSION LIMIT(S)**

NA

**II. MATERIAL LIMIT(S)**

1. The permittee shall not use cleaning solvents containing more than five percent by weight of the following halogenated compounds: methylene chloride, perchloroethylene, trichloroethylene, 1,1,1‑trichloroethane, carbon tetrachloride, chloroform, or any combination thereof. **(R 336.1213(2))**

**III. PROCESS/OPERATIONAL RESTRICTION(S)**

1. Cleaned parts shall be drained for no less than 15 seconds or until dripping ceases. **(R 336.1611(2)(b), R 336.1707(3)(b))**

2. The permittee shall perform routine maintenance on each cold cleaner as recommended by the manufacturer. **(R 336.1213(3))**

**IV. DESIGN/EQUIPMENT PARAMETER(S)**

1. The cold cleaner must meet one of the following design requirements:

a. The air/vapor interface of the cold cleaner is no more than ten square feet. **(R 336.1281(2)(h))**

b. The cold cleaner is used for cleaning metal parts and the emissions are released to the general in-plant environment. **(R 336.1285(2)(r)(iv))**

2. The cold cleaner shall be equipped with a device for draining cleaned parts. **(R 336.1611(2)(b), R 336.1707(3)(b))**

3. All new and existing cold cleaners shall be equipped with a cover and the cover shall be closed whenever parts are not being handled in the cold cleaner. **(R 336.1611(2)(a), R 336.1707(3)(a))**

4. The cover of a new cold cleaner shall be mechanically assisted if the Reid vapor pressure of the solvent is more than 0.3 psia or if the solvent is agitated or heated. **(R 336.1707(3)(a))**

5. If the Reid vapor pressure of any solvent used in a new cold cleaner is greater than 0.6 psia; or, if any solvent used in a new cold cleaner is heated above 120 degrees Fahrenheit, then the cold cleaner must comply with at least one of the following provisions:

a. The cold cleaner must be designed such that the ratio of the freeboard height to the width of the cleaner is equal to or greater than 0.7. **(R 336.1707(2)(a))**

b. The solvent bath must be covered with water if the solvent is insoluble and has a specific gravity of more than 1.0. **(R 336.1707(2)(b))**

c. The cold cleaner must be controlled by a carbon adsorption system, condensation system, or other method of equivalent control approved by the AQD. **(R 336.1707(2)(c))**

**V. TESTING/SAMPLING**

Records shall be maintained on file for a period of five years. **(R 336.1213(3)(b)(ii))**

NA

**VI. MONITORING/RECORDKEEPING**

Records shall be maintained on file for a period of five years. **(R 336.1213(3)(b)(ii))**

1. For each new cold cleaner in which the solvent is heated, the solvent temperature shall be monitored and recorded at least once each calendar week during routine operating conditions. **(R 336.1213(3))**

2. The permittee shall maintain the following information on file for each cold cleaner: **(R 336.1213(3))**

a. A serial number, model number, or other unique identifier for each cold cleaner.

b. The date the unit was installed, manufactured or that it commenced operation.

c. The air/vapor interface area for any unit claimed to be exempt under Rule 281(2)(h).

d. The applicable Rule 201 exemption.

e. The Reid vapor pressure of each solvent used.

f. If applicable, the option chosen to comply with Rule 707(2).

3. The permittee shall maintain written operating procedures for each cold cleaner. These written procedures shall be posted in an accessible, conspicuous location near each cold cleaner. **(R 336.1611(3), R 336.1707(4))**

4. As noted in Rule 611(2)(c) and Rule 707(3)(c), if applicable, an initial demonstration that the waste solvent is a safety hazard shall be made prior to storage in non-closed containers. If the waste solvent is a safety hazard and is stored in non-closed containers, verification that the waste solvent is disposed of so that not more than 20 percent, by weight, is allowed to evaporate into the atmosphere shall be made on a monthly basis. **(R 336.1213(3), R 336.1611(2)(c), R 336.1707(3)(c))**

**VII. REPORTING**

1. Prompt reporting of deviations pursuant to General Conditions 21 and 22 of Part A. **(R 336.1213(3)(c)(ii))**

2. Semiannual reporting of monitoring and deviations pursuant to General Condition 23 of Part A. The report shall be postmarked or received by the appropriate AQD District Office by March 15 for reporting period July 1 to December 31 and September 15 for reporting period January 1 to June 30. **(R 336.1213(3)(c)(i))**

3. Annual certification of compliance pursuant to General Conditions 19 and 20 of Part A. The report shall be postmarked or received by the appropriate AQD District Office by March 15 for the previous calendar year. **(R 336.1213(4)(c))**

**See Appendix 8**

**VIII. STACK/VENT RESTRICTION(S)**

NA

**IX. OTHER REQUIREMENT(S)**

NA

# E. NON-APPLICABLE REQUIREMENTS

At the time of the ROP issuance, the AQD has determined that no non-applicable requirements have been identified for incorporation into the permit shield provision set forth in the General Conditions in Part A pursuant to Rule 213(6)(a)(ii).

|  |
| --- |
| **APPENDICES** |

## Appendix 1. Acronyms and Abbreviations

|  |  |  |  |
| --- | --- | --- | --- |
| **Common Acronyms** | | **Pollutant / Measurement Abbreviations** | |
| AQD | Air Quality Division | acfm | Actual cubic feet per minute |
| BACT | Best Available Control Technology | BTU | British Thermal Unit |
| CAA | Clean Air Act | °C | Degrees Celsius |
| CAM | Compliance Assurance Monitoring | CO | Carbon Monoxide |
| CEM | Continuous Emission Monitoring | CO2e | Carbon Dioxide Equivalent |
| CFR | Code of Federal Regulations | dscf | Dry standard cubic foot |
| COM | Continuous Opacity Monitoring | dscm | Dry standard cubic meter |
| Department/  department | Michigan Department of Environmental Quality | °F | Degrees Fahrenheit |
| gr | Grains |
| EU | Emission Unit | HAP | Hazardous Air Pollutant |
| FG | Flexible Group | Hg | Mercury |
| GACS | Gallons of Applied Coating Solids | hr | Hour |
| GC | General Condition | HP | Horsepower |
| GHGs | Greenhouse Gases | H2S | Hydrogen Sulfide |
| HVLP | High Volume Low Pressure\* | kW | Kilowatt |
| ID | Identification | lb | Pound |
| IRSL | Initial Risk Screening Level | m | Meter |
| ITSL | Initial Threshold Screening Level | mg | Milligram |
| LAER | Lowest Achievable Emission Rate | mm | Millimeter |
| MACT | Maximum Achievable Control Technology | MM | Million |
| MAERS | Michigan Air Emissions Reporting System | MW | Megawatts |
| MAP | Malfunction Abatement Plan | NMOC | Non-methane Organic Compounds |
| MDEQ | Michigan Department of Environmental Quality | NOx | Oxides of Nitrogen |
| ng | Nanogram |
| MSDS | Material Safety Data Sheet | PM | Particulate Matter |
| NA | Not Applicable | PM10 | Particulate Matter equal to or less than 10 microns in diameter |
| NAAQS | National Ambient Air Quality Standards |
| NESHAP | National Emission Standard for Hazardous Air Pollutants | PM2.5 | Particulate Matter equal to or less than 2.5  microns in diameter |
| NSPS | New Source Performance Standards | pph | Pounds per hour |
| NSR | New Source Review | ppm | Parts per million |
| PS | Performance Specification | ppmv | Parts per million by volume |
| PSD | Prevention of Significant Deterioration | ppmw | Parts per million by weight |
| PTE | Permanent Total Enclosure | % | Percent |
| PTI | Permit to Install | psia | Pounds per square inch absolute |
| RACT | Reasonable Available Control Technology | psig | Pounds per square inch gauge |
| ROP | Renewable Operating Permit | scf | Standard cubic feet |
| SC | Special Condition | sec | Seconds |
| SCR | Selective Catalytic Reduction | SO2 | Sulfur Dioxide |
| SNCR | Selective Non-Catalytic Reduction | TAC | Toxic Air Contaminant |
| SRN | State Registration Number | Temp | Temperature |
| TEQ | Toxicity Equivalence Quotient | THC | Total Hydrocarbons |
| USEPA/EPA | United States Environmental Protection Agency | tpy | Tons per year |
| VE | Visible Emissions | µg | Microgram |
| µm | Micrometer or Micron |
|  |  | VOC | Volatile Organic Compounds |
|  |  | yr | Year |

\*For HVLP applicators, the pressure measured at the gun air cap shall not exceed 10 psig.

## Appendix 2. Schedule of Compliance

The permittee certified in the ROP application that this stationary source is in compliance with all applicable requirements and the permittee shall continue to comply with all terms and conditions of this ROP. A Schedule of Compliance is not required. **(R 336.1213(4)(a), R 336.1119(a)(ii))**

## Appendix 3. Monitoring Requirements

Specific monitoring requirement procedures, methods or specifications are detailed in Part A or the appropriate Source-Wide, Emission Unit and/or Flexible Group Special Conditions. Therefore, this appendix is not applicable.

## Appendix 4. Recordkeeping

Specific recordkeeping requirement formats and procedures are detailed in Part A or the appropriate Source-Wide, Emission Unit and/or Flexible Group Special Conditions. Therefore, this appendix is not applicable.

## Appendix 5. Testing Procedures

Specific testing requirement plans, procedures, and averaging times are detailed in the appropriate Source-Wide, Emission Unit and/or Flexible Group Special Conditions. Therefore, this appendix is not applicable.

## Appendix 6. Permits to Install

The following table lists any PTIs issued or ROP revision applications received since the effective date of the previously issued ROP No. MI-ROP-B7287-2014 Those ROP revision applications that are being issued concurrently with this ROP renewal are identified by an asterisk (\*). Those revision applications not listed with an asterisk were processed prior to this renewal.

Source-Wide PTI No MI-PTI-B7287-2014 is being reissued as Source-Wide PTI No. MI-PTI-B7287-20XX.

|  |  |  |  |
| --- | --- | --- | --- |
| **Permit to Install Number** | **ROP Revision**  **Application Number** | **Description of Equipment or Change** | **Corresponding Emission Unit(s) or**  **Flexible Group(s)** |
| NA | NA | NA | NA |

## Appendix 7. Emission Calculations

There are no specific emission calculations to be used for this ROP. Therefore, this appendix is not applicable.

## Appendix 8. Reporting

**A. Annual, Semiannual, and Deviation Certification Reporting**

The permittee shall use the MDEQ, AQD, Report Certification form (EQP 5736) and MDEQ, AQD, Deviation Report form (EQP 5737) for the annual, semiannual and deviation certification reporting referenced in the Reporting Section of the Source-Wide, Emission Unit and/or Flexible Group Special Conditions. Alternative formats must meet the provisions of Rule 213(4)(c) and Rule 213(3)(c)(i), respectively, and be approved by the AQD District Supervisor.

**B. Other Reporting**

Specific reporting requirement formats and procedures are detailed in Part A or the appropriate Source-Wide, Emission Unit and/or Flexible Group Special Conditions. Therefore, Part B of this appendix is not applicable.